## Data
Moyle Interconnector Ltd | [9 empty] | Updated | 2016-11-16
Record of historic and planned outages
Outages entered following completion and when planned dates agreed with System Operator
Moyle indicatively plan a 48hr outage on one pole (160MW capacity loss) per year during summer months
Scottish power indicatively plan for 24hour line outage every two years (410MW capacity loss) during summer months
Planned outage: | Outages for planned works which are notified to SONI in accordance with Grid Code and also notified to users well in advance.
Scheduled outage: | Outages for ahhoc non-urgent works which can be notified to users and scheduled for period of low usage.
Forced outage: | Unexpected outage, usually due to a technical fault.
=Actual date
=Forecast date
Maximum Import Capacity: | East to West |  | November - March 450MW : April - October 410MW
Maximum Export Capacity | West to East |  | September - April 295MW : May - August 287MW
Start date | End date |  | Affected pole |  | Fault description | Maximum import capacity | Maximum export capacity | Outage duration | Max import equivalent Outage Duration | Estimated loss of scheduled transfer | Import Capacity loss | Export Capacity loss | Import Capacity available | Export Capacity available | Outage Type (Scheduled - SO, Forced - FO, Planned - PO) | Equivalent outage durations annual totals
|  |  | 1 | 2 |  | MW | MW | Hours | Hours | MW | MW | MW | MW | MW |  | SO | FO | PO
2004-04-01 | 2004-04-01 01:07 | 2005-04-01 | Y | Y | 100 Hz DC Protection | 400 | 80 | 1.12 | 1.12 | n/a | 400 | 80 | 0 | 0 | FO |  |  |  | 0 | 1.12 | 0 | 2004 | 4 | 1
2004-04-05 | 2004-04-05 00:37 | 2005-04-01 | Y |  | 100 Hz DC Protection | 400 | 80 | 0.62 | 0.31 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 0 | 1.43 | 0 | 2004 | 4 | 1
2004-04-06 | 2004-04-06 00:23 | 2005-04-01 | Y | Y | 100 Hz DC Protection | 400 | 80 | 0.38 | 0.38 | n/a | 400 | 80 | 0 | 0 | FO |  |  |  | 0 | 1.81 | 0 | 2004 | 4 | 1
2004-07-10 | 2004-07-10 09:25 | 2005-04-01 | Y | Y | Scottish Power OHL work and Bi-annual pole maintenance | 400 | 80 | 9.41 | 9.41 | n/a | 400 | 80 | 0 | 0 | SO |  |  |  | 9.41 | 1.81 | 0 | 2004 | 7 | 4
2004-07-11 | 2004-07-12 | 2005-04-01 | Y | Y | Scottish Power OHL work and Bi-annual pole maintenance | 400 | 80 | 24 | 24 | n/a | 400 | 80 | 0 | 0 | SO |  |  |  | 33.41 | 1.81 | 0 | 2004 | 7 | 4
2004-07-12 | 2004-07-13 | 2005-04-01 | Y | Y | Scottish Power OHL work and Bi-annual pole maintenance | 400 | 80 | 24 | 24 | n/a | 400 | 80 | 0 | 0 | SO |  |  |  | 57.41 | 1.81 | 0 | 2004 | 7 | 4
2004-07-13 | 2004-07-14 | 2005-04-01 | Y | Y | Scottish Power OHL work and Bi-annual pole maintenance | 400 | 80 | 24 | 24 | n/a | 400 | 80 | 0 | 0 | SO |  |  |  | 81.41 | 1.81 | 0 | 2004 | 7 | 4
2004-07-14 | 2004-07-14 09:25 | 2005-04-01 | Y | Y | Scottish Power OHL work and Bi-annual pole maintenance | 400 | 80 | 9.41 | 9.41 | n/a | 400 | 80 | 0 | 0 | SO |  |  |  | 90.82 | 1.81 | 0 | 2004 | 7 | 4
2004-07-16 | 2004-07-16 02:35 | 2005-04-01 | Y |  | Pole block due to filter trip | 400 | 80 | 2.58 | 1.29 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 90.82 | 3.1 | 0 | 2004 | 7 | 4
2004-09-03 | 2004-09-03 00:24 | 2005-04-01 |  | Y | Light emitter card deferred maintenance | 400 | 80 | 0.4 | 0.2 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 91.02 | 3.1 | 0 | 2004 | 9 | 6
2004-09-03 | 2004-09-03 00:40 | 2005-04-01 | Y |  | Light receiver card deferred maintenance | 400 | 80 | 0.66 | 0.33 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 91.35 | 3.1 | 0 | 2004 | 9 | 6
2004-10-01 | 2004-10-01 00:53 | 2005-04-01 | Y |  | Pole block due to filter trip | 400 | 80 | 0.88 | 0.44 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 91.35 | 3.54 | 0 | 2004 | 10 | 7
2004-10-03 | 2004-10-03 06:37 | 2005-04-01 |  | Y | Filter Upgrade; Lightning conductor removal | 400 | 80 | 6.62 | 3.31 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 94.66 | 3.54 | 0 | 2004 | 10 | 7
2004-10-29 | 2004-10-29 00:16 | 2005-04-01 | Y |  | Light receiver card deferred maintenance | 400 | 80 | 0.26 | 0.13 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 94.79 | 3.54 | 0 | 2004 | 10 | 7
2004-11-10 | 2004-11-10 00:32 | 2005-04-01 |  | Y | Maloperation | 400 | 80 | 0.54 | 0.27 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 94.79 | 3.81 | 0 | 2004 | 11 | 8
2004-11-14 | 2004-11-14 08:55 | 2005-04-01 |  | Y | Filter Upgrade; Lightning conductor replacement | 400 | 80 | 8.92 | 4.46 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 99.25 | 3.81 | 0 | 2004 | 11 | 8
2004-11-14 | 2004-11-14 00:23 | 2005-04-01 | Y |  | 100 Hz DC Protection | 400 | 80 | 0.38 | 0.19 | n/a | 150 | 0 | 250 | 80 | FO | 99.25 | 4 | 0 | 99.25 | 4 | 0 | 2004 | 11 | 8
2005-05-05 | 2005-05-05 01:26 | 2006-04-01 | Y |  | Light receiver card | 400 | 80 | 1.44 | 0.72 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 0 | 0.72 | 0 | 2005 | 5 | 2
2005-05-10 | 2005-05-10 08:30 | 2006-04-01 | Y |  | Pole block due to filter trips | 400 | 80 | 8.5 | 4.25 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 0 | 4.97 | 0 | 2005 | 5 | 2
2005-05-11 | 2005-05-11 04:24 | 2006-04-01 | Y |  | VBE System Fault | 400 | 80 | 4.4 | 2.2 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 0 | 7.17 | 0 | 2005 | 5 | 2
2005-05-13 | 2005-05-13 00:07 | 2006-04-01 | Y |  | Pole block due to filter trips | 400 | 80 | 0.12 | 0.06 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 0 | 7.23 | 0 | 2005 | 5 | 2
2005-05-23 | 2005-05-23 19:30 | 2006-04-01 |  | Y | Transformer condition assessment | 400 | 80 | 19.5 | 9.75 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 9.75 | 7.23 | 0 | 2005 | 5 | 2
2005-05-24 | 2005-05-25 | 2006-04-01 |  | Y | Transformer condition assessment | 400 | 80 | 24 | 12 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 21.75 | 7.23 | 0 | 2005 | 5 | 2
2005-05-25 | 2005-05-25 19:30 | 2006-04-01 |  | Y | Transformer condition assessment | 400 | 80 | 19.5 | 9.75 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 31.5 | 7.23 | 0 | 2005 | 5 | 2
2005-06-13 | 2005-06-13 15:15 | 2006-04-01 | Y |  | Transformer condition assessment | 400 | 80 | 15.25 | 7.625 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 39.125 | 7.23 | 0 | 2005 | 6 | 3
2005-06-14 | 2005-06-15 | 2006-04-01 | Y |  | Transformer condition assessment | 400 | 80 | 24 | 12 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 51.125 | 7.23 | 0 | 2005 | 6 | 3
2005-06-15 | 2005-06-15 15:15 | 2006-04-01 | Y |  | Transformer condition assessment | 400 | 80 | 15.25 | 7.625 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 58.75 | 7.23 | 0 | 2005 | 6 | 3
2005-06-19 | 2005-06-19 12:00 | 2006-04-01 |  | Y | Vesda fire detection fault | 400 | 80 | 12 | 6 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 58.75 | 13.23 | 0 | 2005 | 6 | 3
2005-06-20 | 2005-06-20 02:18 | 2006-04-01 | Y |  | Control oscillation following wiring mod | 400 | 80 | 2.3 | 1.15 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 58.75 | 14.38 | 0 | 2005 | 6 | 3
2005-06-20 | 2005-06-20 00:10 | 2006-04-01 | Y |  | Pole block due to filter trips | 400 | 80 | 0.16 | 0.08 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 58.75 | 14.46 | 0 | 2005 | 6 | 3
2005-06-21 | 2005-06-21 00:20 | 2006-04-01 | Y | Y | Power reversal testing | 400 | 80 | 0.34 | 0.34 | n/a | 400 | 80 | 0 | 0 | SO |  |  |  | 59.09 | 14.46 | 0 | 2005 | 6 | 3
2005-07-12 | 2005-07-12 23:33 | 2006-04-01 | Y |  | Bi-annual pole maintenance | 400 | 80 | 23.55 | 11.775 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 70.865 | 14.46 | 0 | 2005 | 7 | 4
2005-07-12 | 2005-07-12 03:12 | 2006-04-01 |  | Y | Maloperation on valve cooling | 400 | 80 | 3.2 | 1.6 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 70.865 | 16.06 | 0 | 2005 | 7 | 4
2005-07-13 | 2005-07-13 23:33 | 2006-04-01 | Y |  | Bi-annual pole maintenance | 400 | 80 | 23.55 | 11.775 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 82.64 | 16.06 | 0 | 2005 | 7 | 4
2005-07-18 | 2005-07-18 09:00 | 2006-04-01 | Y |  | Pole block due to filter trips | 400 | 80 | 9 | 4.5 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 82.64 | 20.56 | 0 | 2005 | 7 | 4
2005-08-03 | 2005-08-03 02:00 | 2006-04-01 |  | Y | BETTA wiring and testing | 400 | 80 | 2 | 1 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 83.64 | 20.56 | 0 | 2005 | 8 | 5
2005-08-03 | 2005-08-03 04:30 | 2006-04-01 | Y |  | Protection trip on return to service following BETTA wiring mods | 400 | 80 | 4.5 | 2.25 | n/a | 150 | 0 | 250 | 80 | FO |  |  |  | 83.64 | 22.81 | 0 | 2005 | 8 | 5
2005-09-13 | 2005-09-13 01:53 | 2006-04-01 | Y |  | BETTA wiring and testing | 400 | 80 | 1.88 | 0.94 | n/a | 150 | 0 | 250 | 80 | SO |  |  |  | 84.58 | 22.81 | 0 | 2005 | 9 | 6
2005-09-13 | 2005-09-13 00:12 | 2006-04-01 | Y |  | Trip due to AC filter after BETTA wiring mods | 400 | 80 | 0.2 | 0.1 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 84.58 | 22.91 | 0 | 2005 | 9 | 6
2005-10-13 | 2005-10-13 01:42 | 2006-04-01 |  | Y | Pole block due to filter trips | 400 | 80 | 1.7 | 0.85 | 45 | 150 | 0 | 250 | 80 | FO |  |  |  | 84.58 | 23.76 | 0 | 2005 | 10 | 7
2005-10-26 | 2005-10-26 02:07 | 2006-04-01 |  | Y | Pole block due to filter trips | 400 | 80 | 2.12 | 1.06 | 45 | 150 | 0 | 250 | 80 | FO | 84.58 | 24.82 | 0 | 84.58 | 24.82 | 0 | 2005 | 10 | 7
2006-04-02 | 2006-04-02 16:45 | 2007-04-01 | Y | Y | Scottish Power overhead line maintenance | 400 | 80 | 16.75 | 16.75 | 200 | 400 | 80 | 0 | 0 | SO |  |  |  | 16.75 | 0 | 0 | 2006 | 4 | 1
2006-04-03 | 2006-04-03 16:45 | 2007-04-01 | Y | Y | Scottish Power overhead line maintenance | 400 | 80 | 16.75 | 16.75 | 200 | 400 | 80 | 0 | 0 | SO |  |  |  | 33.5 | 0 | 0 | 2006 | 4 | 1
2006-06-27 | 2006-06-27 00:46 | 2007-04-01 | Y |  | 50Hz protection | 400 | 80 | 0.76 | 0.38 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 33.5 | 0.38 | 0 | 2006 | 6 | 3
2006-06-29 | 2006-06-29 04:44 | 2007-04-01 |  | Y | VBE System microcontroller | 400 | 80 | 4.74 | 2.37 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 33.5 | 2.75 | 0 | 2006 | 6 | 3
2006-06-29 | 2006-06-29 01:00 | 2007-04-01 |  | Y | Light receiver card | 400 | 80 | 1 | 0.5 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 33.5 | 3.25 | 0 | 2006 | 6 | 3
2006-07-12 | 2006-07-12 19:04 | 2007-04-01 |  | Y | Bi-annual pole maintenance | 400 | 80 | 19.06 | 9.53 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 43.03 | 3.25 | 0 | 2006 | 7 | 4
2006-07-13 | 2006-07-13 19:04 | 2007-04-01 |  | Y | Bi-annual pole maintenance | 400 | 80 | 19.06 | 9.53 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 52.56 | 3.25 | 0 | 2006 | 7 | 4
2006-07-13 | 2006-07-13 02:10 | 2007-04-01 | Y |  | Breaker fail protection | 400 | 80 | 2.16 | 1.08 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 52.56 | 4.33 | 0 | 2006 | 7 | 4
2006-07-25 | 2006-07-25 01:12 | 2007-04-01 | Y |  | Valve cooling- terminal hotspot | 400 | 80 | 1.2 | 0.6 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 53.16 | 4.33 | 0 | 2006 | 7 | 4
2006-08-16 | 2006-08-16 01:30 | 2007-04-01 |  | Y | Valve cooling high conductivity | 400 | 80 | 1.5 | 0.75 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 53.91 | 4.33 | 0 | 2006 | 8 | 5
2006-08-16 | 2006-08-16 00:48 | 2007-04-01 |  | Y | Maloperation on DC protection system | 400 | 80 | 0.8 | 0.4 | 0 | 150 | 0 | 250 | 80 | FO |  |  |  | 53.91 | 4.73 | 0 | 2006 | 8 | 5
2006-08-16 | 2006-08-16 05:31 | 2007-04-01 |  | Y | Valve cooling pump leak | 400 | 80 | 5.52 | 2.76 | 85 | 150 | 0 | 250 | 80 | FO |  |  |  | 53.91 | 7.49 | 0 | 2006 | 8 | 5
2006-08-25 | 2006-08-25 01:55 | 2007-04-01 |  | Y | DC Yard Transducer replacement | 400 | 80 | 1.92 | 0.96 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 54.87 | 7.49 | 0 | 2006 | 8 | 5
2006-12-04 | 2006-12-04 00:58 | 2007-04-01 | Y |  | Valve cooling replace plc | 400 | 80 | 0.96 | 0.48 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 55.35 | 7.49 | 0 | 2006 | 12 | 9
2006-12-13 | 2006-12-13 06:00 | 2007-04-01 |  | Y | Wind damage to roof precautionary outage | 400 | 80 | 6 | 3 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 58.35 | 7.49 | 0 | 2006 | 12 | 9
2006-12-14 | 2006-12-14 19:36 | 2007-04-01 |  | Y | Wind damage to roof precautionary outage | 400 | 80 | 19.6 | 9.8 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 68.15 | 7.49 | 0 | 2006 | 12 | 9
2007-01-18 | 2007-01-18 01:36 | 2007-04-01 | Y | Y | Software - emergency support upgrades | 400 | 80 | 1.6 | 1.6 | 0 | 400 | 80 | 0 | 0 | SO |  |  |  | 69.75 | 7.49 | 0 | 2007 | 1 | 10
2007-01-19 | 2007-01-19 01:36 | 2007-04-01 | Y | Y | Software - emergency support upgrades | 400 | 80 | 1.6 | 1.6 | 0 | 400 | 80 | 0 | 0 | SO |  |  |  | 71.35 | 7.49 | 0 | 2007 | 1 | 10
2007-02-05 | 2007-02-05 02:11 | 2007-04-01 | Y |  | Commutation failure | 400 | 80 | 2.18 | 1.09 | 85 | 150 | 0 | 250 | 80 | FO |  |  |  | 71.35 | 8.58 | 0 | 2007 | 2 | 11
2007-02-05 | 2007-02-05 01:36 | 2007-04-01 | Y |  | Commutation / Light emitter failure | 400 | 80 | 1.6 | 0.8 | 85 | 150 | 0 | 250 | 80 | FO | 71.35 | 9.38 | 0 | 71.35 | 9.38 | 0 | 2007 | 2 | 11
2007-04-04 | 2007-04-04 00:44 | 2008-04-01 |  | Y | Tap changer out of sequence | 400 | 80 | 0.74 | 0.37 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 0.37 | 0 | 0 | 2007 | 4 | 1
2007-04-24 | 2007-04-24 02:30 | 2008-04-01 | Y |  | Tap changer clearance distance measurement | 400 | 80 | 2.5 | 1.25 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 1.62 | 0 | 0 | 2007 | 4 | 1
2007-07-12 | 2007-07-12 20:30 | 2008-04-01 | Y |  | Bi-annual pole maintenance | 400 | 80 | 20.5 | 10.25 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 11.87 | 0 | 0 | 2007 | 7 | 4
2007-07-13 | 2007-07-13 20:30 | 2008-04-01 | Y |  | Bi-annual pole maintenance | 400 | 80 | 20.5 | 10.25 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 22.12 | 0 | 0 | 2007 | 7 | 4
2007-07-13 | 2007-07-13 03:22 | 2008-04-01 | Y |  | High valve cooling water conductivity following planned outage | 400 | 80 | 3.3654 | 1.75 | 0 | 160 | 0 | 240 | 80 | FO |  |  |  | 22.12 | 1.75 | 0 | 2007 | 7 | 4
2007-07-14 | 2007-07-14 18:31 | 2008-04-01 | Y |  | High valve cooling water conductivity following planned outage | 400 | 80 | 18.5192 | 9.63 | 0 | 160 | 0 | 240 | 80 | FO |  |  |  | 22.12 | 11.38 | 0 | 2007 | 7 | 4
2007-07-15 | 2007-07-15 04:52 | 2008-04-01 | Y |  | No check back signal | 400 | 80 | 4.86 | 2.43 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 24.55 | 11.38 | 0 | 2007 | 7 | 4
2007-07-15 | 2007-07-15 01:19 | 2008-04-01 | Y |  | Links to be removed from TVM Card | 400 | 80 | 1.32 | 0.66 | 0 | 150 | 0 | 250 | 80 | SO |  |  |  | 25.21 | 11.38 | 0 | 2007 | 7 | 4
2007-11-28 | 2007-11-28 02:11 | 2008-04-01 | Y |  | DC measurement card deferred maintenance | 450 | 80 | 2.18 | 1.09 | 0 | 200 | 0 | 250 | 80 | SO |  |  |  | 26.3 | 11.38 | 0 | 2007 | 11 | 8
2008-02-07 | 2008-02-07 01:00 | 2008-04-01 | Y |  | DC measurement card deferred maintenance | 450 | 80 | 1 | 0.5 | 0 | 200 | 0 | 250 | 80 | SO |  |  |  | 26.8 | 11.38 | 0 | 2008 | 2 | 11
2008-02-07 | 2008-02-07 07:05 | 2008-04-01 | Y |  | No check back signal | 450 | 80 | 7.08 | 3.54 | 0 | 200 | 0 | 250 | 80 | FO |  |  |  | 26.8 | 14.92 | 0 | 2008 | 2 | 11
2008-02-08 | 2008-02-08 01:00 | 2008-04-01 |  | Y | DC measurement card deferred maintenance | 450 | 80 | 1 | 0.5 | 0 | 200 | 0 | 250 | 80 | SO |  |  |  | 27.3 | 14.92 | 0 | 2008 | 2 | 11
2008-03-02 | 2008-03-02 01:26 | 2008-04-01 |  | Y | Valve cooling temperature probe fault | 450 | 80 | 1.44 | 0.72 | 0 | 200 | 0 | 250 | 80 | FO |  |  |  | 27.3 | 15.64 | 0 | 2008 | 3 | 12
2008-03-02 | 2008-03-02 00:37 | 2008-04-01 |  | Y | Valve cooling temperature probe fault | 450 | 80 | 0.62 | 0.31 | 0 | 200 | 0 | 250 | 80 | FO | 27.3 | 15.95 | 0 | 27.3 | 15.95 | 0 | 2008 | 3 | 12
2008-05-12 23:52 | 2008-05-13 04:26 | 2009-04-01 | Y |  | Transformer pressure switch wiring | 410 | 80 | 4.56 | 2.28 | 0 | 160 | 0 | 250 | 80 | SO |  |  |  | 2.28 | 0 | 0 | 2008 | 5 | 2
2008-06-11 14:20 | 2008-06-11 14:40 | 2009-04-01 |  | Y | Cooling water pump 1 test run | 410 | 80 | 0.33 | 0.165 | 0 | 160 | 0 | 250 | 80 | SO |  |  |  | 2.445 | 0 | 0 | 2008 | 6 | 3
2008-06-23 19:36 | 2008-06-23 22:32 | 2009-04-01 |  | Y | Cooling water temperature probe software modification | 410 | 80 | 2.93 | 1.465 | 0 | 160 | 0 | 250 | 80 | SO |  |  |  | 3.91 | 0 | 0 | 2008 | 6 | 3
2008-06-23 11:43 | 2008-06-23 13:23 | 2009-04-01 | Y |  | Cooling water temperature probe software modification | 410 | 80 | 1.67 | 0.835 | 0 | 160 | 0 | 250 | 80 | SO |  |  |  | 4.745 | 0 | 0 | 2008 | 6 | 3
2008-08-05 15:14 | 2008-08-05 17:14 | 2009-04-01 | Y | Y | Scottish Power line outage - only one high speed protection available | 410 | 80 | 1.993 | 1.993 | 75 | 410 | 80 | 0 | 0 | SO |  |  |  | 6.738 | 0 | 0 | 2008 | 8 | 5
2008-08-23 06:00 | 2008-08-24 06:00 | 2009-04-01 | Y | Y | Scottish Power overhead line maintenance & Bi-annual pole maintenance | 410 | 80 | 24 | 24 |  | 410 | 80 | 0 | 0 | PO |  |  |  | 6.738 | 0 | 24 | 2008 | 8 | 5
2008-08-23 04:30 | 2008-08-24 04:00 | 2009-04-01 | Y | Y | Scottish Power overhead line maintenance & Bi-annual pole maintenance | 410 | 80 | 23.5 | 23.5 | 55 | 410 | 80 | 0 | 0 | SO |  |  |  | 30.238 | 0 | 24 | 2008 | 8 | 5
2008-08-24 04:30 | 2008-08-25 04:30 | 2009-04-01 |  | Y | Bi-annual pole maintenance | 410 | 80 | 24 | 12 |  | 160 | 0 | 250 | 80 | PO |  |  |  | 30.238 | 0 | 36 | 2008 | 8 | 5
2008-08-24 06:00 | 2008-08-25 11:30 | 2009-04-01 |  | Y | Bi-annual pole maintenance | 410 | 80 | 29.5 | 14.75 | 0 | 160 | 0 | 250 | 80 | SO |  |  |  | 44.988 | 0 | 36 | 2008 | 8 | 5
2008-09-02 06:00 | 2008-09-02 06:30 | 2009-04-01 | Y |  | Light emitter card | 410 | 80 | 0.5 | 0.25 | 0 | 160 | 0 | 250 | 80 | SO |  |  |  | 45.238 | 0 | 36 | 2008 | 9 | 6
2008-11-22 | 2008-11-22 01:50 | 2009-04-01 |  | Y | Static Reserve direction problem | 410 | 80 | 1.84 | 0.92 | 0 | 160 | 0 | 250 | 80 | FO |  |  |  | 45.238 | 0.92 | 36 | 2008 | 11 | 8
2009-01-13 09:01 | 2009-01-13 10:54 | 2009-04-01 |  | Y | DC measuring equipment fault | 450 | 80 | 1.8833 | 0.94167 | 0 | 200 | 0 | 250 | 80 | SO | 46.1797 | 0.92 | 36 | 46.1797 | 0.92 | 36 | 2009 | 1 | 10
2009-06-01 00:02 | 2009-06-01 10:26 | 2010-04-01 | Y |  | Valve cooling control interface unit fault | 410 | 80 | 10.4 | 5.2 | 9.0476 | 160 | 0 | 250 | 80 | FO |  |  |  | 0 | 5.2 | 0 | 2009 | 6 | 3
2009-06-08 12:52 | 2009-06-08 13:59 | 2010-04-01 | Y | Y | Operator error | 410 | 80 | 1.1167 | 1.1167 | 409 | 410 | 80 | 0 | 0 | FO |  |  |  | 0 | 6.3167 | 0 | 2009 | 6 | 3
2009-07-02 06:30 | 2009-07-02 20:40 | 2010-04-01 |  | Y | DC measuring equipment fault | 410 | 80 | 14.1667 | 7.0833 | 24.0706 | 160 | 0 | 250 | 80 | FO |  |  |  | 0 | 13.4 | 0 | 2009 | 7 | 4
2009-07-13 18:25 | 2009-07-13 21:12 | 2010-04-01 |  | Y | Transformer winding current measurement equipment fault | 410 | 80 | 2.775 | 1.3875 | 140 | 160 | 0 | 250 | 80 | FO |  |  |  | 0 | 14.7875 | 0 | 2009 | 7 | 4
2009-09-28 08:00 | 2009-10-09 18:00 | 2010-04-01 | Y | Y | Scottish Power line outage to connect wind farms and Pole 2 biannual outage | 410 | 80 | 274 | 274 | 290 | 410 | 80 | 0 | 0 | SO |  |  |  | 274 | 14.7875 | 0 | 2009 | 9 | 6
2009-10-12 17:38 | 2009-10-12 20:07 | 2010-04-01 |  | Y | Uninterruptable power supply fault | 410 | 80 | 2.48 | 1.24 | 80.5 | 160 | 0 | 250 | 80 | FO |  |  |  | 274 | 16.0275 | 0 | 2009 | 10 | 7
2009-10-16 17:38 | 2009-10-16 18:13 | 2010-04-01 | Y |  | Transformer monitoring unit fault | 410 | 80 | 0.58 | 0.29 | 128 | 160 | 0 | 250 | 80 | FO |  |  |  | 274 | 16.3175 | 0 | 2009 | 10 | 7
2009-12-01 17:55 | 2009-12-01 20:40 | 2010-04-01 |  | Y | Valve cooling high water conductivity | 450 | 80 | 2.746 | 1.373 | 171.4 | 200 | 0 | 250 | 80 | FO |  |  |  | 274 | 17.6905 | 0 | 2009 | 12 | 9
2009-12-21 15:36 | 2009-12-21 17:36 | 2010-04-01 | Y |  | Transformer oil weep inspection | 450 | 80 | 2.0086 | 1.0043 | 0 | 200 | 0 | 250 | 80 | SO |  |  |  | 275.0043 | 17.6905 | 0 | 2009 | 12 | 9
2010-01-06 16:04 | 2010-01-06 16:39 | 2010-04-01 | Y |  | Fire monitoring system fault | 450 | 80 | 0.58333 | 0.29167 | 263 | 200 | 0 | 250 | 80 | FO |  |  |  | 275.0043 | 17.9822 | 0 | 2010 | 1 | 10
2010-01-21 18:37 | 2010-01-22 02:41 | 2010-04-01 |  | Y | Valve cooling high water conductivity | 450 | 80 | 8.0667 | 4.0333 | 135 | 200 | 0 | 250 | 80 | FO |  |  |  | 275.0043 | 22.0155 | 0 | 2010 | 1 | 10
2010-02-16 13:03 | 2010-02-16 13:44 | 2010-04-01 | Y |  | Fire monitoring system fault | 450 | 80 | 0.68 | 0.34 | 179 | 200 | 0 | 250 | 80 | FO |  |  |  | 275.0043 | 22.3555 | 0 | 2010 | 2 | 11
2010-03-30 19:29 | 2010-03-30 21:27 | 2010-04-01 | Y |  | Commutation failure - NI system voltage | 450 | 80 | 1.96 | 0.98 | 179 | 200 | 0 | 250 | 80 | FO |  |  |  | 275.0043 | 23.3355 | 0 | 2010 | 3 | 12
2010-03-30 19:29 | 2010-03-30 20:37 | 2010-04-01 | Y | Y | Commutation failure - NI system voltage | 450 | 80 | 1.13 | 1.13 | 429 | 450 | 80 | 0 | 0 | FO |  |  |  | 275.0043 | 24.4655 | 0 | 2010 | 3 | 12
2010-03-31 00:45 | 2010-03-31 01:10 | 2010-04-01 | Y |  | Commutation failure - NI system voltage | 450 | 80 | 0.42 | 0.21 | 0 | 200 | 0 | 250 | 80 | FO |  |  |  | 275.0043 | 24.6755 | 0 | 2010 | 3 | 12
2010-03-31 01:34 | 2010-03-31 02:17 | 2010-04-01 |  | Y | Commutation failure - NI system voltage | 450 | 80 | 0.72 | 0.36 | 19 | 200 | 0 | 250 | 80 | FO |  |  |  | 275.0043 | 25.0355 | 0 | 2010 | 3 | 12
2010-03-31 08:29 | 2010-03-31 08:39 | 2010-04-01 | Y |  | Commutation failure - NI system voltage | 450 | 80 | 0.16 | 0.08 | 179 | 200 | 0 | 250 | 80 | FO |  |  |  | 275.0043 | 25.1155 | 0 | 2010 | 3 | 12
2010-03-31 08:44 | 2010-03-31 08:58 | 2010-04-01 |  | Y | Commutation failure - NI system voltage | 450 | 80 | 0.24 | 0.12 | 179 | 200 | 0 | 250 | 80 | FO | 275.0043 | 25.2355 | 0 | 275.0043 | 25.2355 | 0 | 2010 | 3 | 12
2010-06-14 | 2010-07-08 | 2011-04-01 | Y | Y | Scottish Power line outage to connect windfarms | 410 | 80 | 576 | 576 | 243 | 410 | 80 | 0 | 0 | PO |  |  |  | 0 | 0 | 576 | 2010 | 6 | 3
2010-09-09 12:41 | 2010-11-01 | 2011-04-01 | Y |  | Cable fault | 410 | 80 | 1259.3167 | 491.4407 | 117 | 160 | 0 | 250 | 80 | FO |  |  |  | 0 | 491.4407 | 576 | 2010 | 9 | 6
2010-11-01 | 2010-11-18 | 2011-04-01 | Y |  | Cable fault | 450 | 80 | 408 | 181.3333 | 146 | 200 | 0 | 250 | 80 | FO |  |  |  | 0 | 672.774 | 576 | 2010 | 11 | 8
2011-11-01 | 2011-11-01 03:10 | 2011-04-01 |  | Y | Conductivity High alarm | 450 | 80 | 3.17 | 1.585 | 0 | 200 | 0 | 250 | 80 | FO |  |  |  | 0 | 674.359 | 576 | 2011 | 11 | 8
2011-03-19 08:30 | 2011-03-19 10:12 | 2011-04-01 |  | Y | Pole Failure To Deblock | 450 | 80 | 1.7 | 0.85 | 31 | 200 | 0 | 250 | 80 | FO | 0 | 675.209 | 576 | 0 | 675.209 | 576 | 2011 | 3 | 12
2011-05-25 15:47 | 2011-05-25 16:48 | 2012-04-01 | Y | Y | Valve cooling issued trip command after Diesel Gen Circuit Breaker Fail (had lost external SP supplies 1 minute earlier) | 410 | 287 | 1.02 | 0.5 | 410 | 410 | 287 | 0 | 0 | FO |  |  |  | 0 | 0.5 | 0 | 2011 | 5 | 2
2011-08-23 | 2011-08-26 | 2012-04-01 | Y |  | Bi-annual pole maintenance | 410 | 287 | 72 | 36 | 0 | 160 | 37 | 250 | 250 | PO | 0 | 0.5 | 36 | 0 | 0.5 | 36 | 2011 | 8 | 5
2011-06-26 04:17 | 2011-08-24 14:00 | 2012-04-01 | Y |  | Cable fault | 410 | 287 | 1425.7167 | 556.3772 | 145 | 160 | 37 | 250 | 250 | FO |  |  |  | 0 | 556.3772 | 0 | 2011 | 6 | 3
2011-08-24 14:00 | 2011-11-01 06:00 | 2012-04-01 | Y | Y | Cable fault | 410 | 287 | 1648 | 1648 | 250 | 410 | 287 | 0 | 0 | FO |  |  |  | 0 | 2204.3772 | 0 | 2011 | 8 | 5
2011-11-01 06:00 | 2012-01-18 21:00 | 2012-04-01 | Y | Y | Cable fault | 450 | 287 | 1887 | 1887 | n/a | 450 | 287 | 0 | 0 | FO |  |  |  | 0 | 4091.3772 | 0 | 2011 | 11 | 8
2012-01-18 21:00 | 2012-02-19 06:00 | 2012-04-01 |  | Y | Cable fault | 450 | 287 | 753 | 376.5 | n/a | 225 | 62 | 225 | 225 | FO | 0 | 4467.8772 | 0 | 0 | 4467.8772 | 0 | 2012 | 1 | 10
2012-06-23 10:17 | 2012-11-01 | 2012-04-01 |  | Y | Cable fault | 410 | 287 | 3133.7164 | 1222.9137 | 136 | 160 | 37 | 250 | 250 | FO |  |  |  | 0 | 1222.9137 | 0 | 2012 | 6 | 3
2012-11-01 | 2013-03-31 |  |  | Y | Cable fault | 450 | 295 | 3600 | 1600 | n/a | 200 | 45 | 250 | 250 | FO | 0 | 2822.9137 | 0 | 0 | 2822.9137 | 0 | 2012 | 11 | 8
2012-08-11 10:22 | 2012-08-11 11:25 |  |  | Y | Station control system 2 trip | 410 | 287 | 1.0475 | 0.63872 | 220 | 250 | 250 | 0 | 0 | FO |  |  |  | 0 | 0.63872 | 0 | 2012 | 8 | 5
2012-09-03 12:03 | 2012-09-04 00:17 |  |  | Y | Re-Configuration Testing | 410 | 287 | 12.2333 | 4.774 | n/a | 160 | 37 | 0 | 0 | PO |  |  |  | 0 | 0.63872 | 4.774 | 2012 | 9 | 6
2012-10-01 08:58 | 2012-10-01 09:46 |  |  | Y | NIE incomer fault which led to a trip in calve cooling | 410 | 287 | 1 | 0.39024 | 178 | 160 | 37 | 0 | 0 | FO |  |  |  | 0 | 1.029 | 4.774 | 2012 | 10 | 7
2012-11-27 06:00 | 2012-11-29 06:00 |  | Y | Y | Re-Configuration Testing | 450 | 295 | 48 | 21.3333 | n/a | 200 | 45 | 0 | 0 | PO |  |  |  | 0 | 1.029 | 26.1073 | 2012 | 11 | 8
2013-01-18 16:38 | 2013-01-18 20:36 |  |  | Y | Commutation failure at Ballycronan more | 450 | 295 | 3.9636 | 1.7616 | n/a | 200 | 45 | 0 | 0 | FO |  |  |  | 0 | 2.7906 | 26.1073 | 2013 | 1 | 10
2013-03-22 00:59 | 2013-03-22 05:07 |  | Y | Y | Commutation failure at Ballycronan more (NI Ice Storm) | 450 | 295 | 4.13 | 1.8356 |  | 200 | 45 | 0 | 0 | FO |  |  |  | 0 | 4.6261 | 26.1073 | 2013 | 3 | 12
2013-03-22 10:49 | 2013-03-22 15:35 |  | Y | Y | Diesel Generator Circuit Breaker Failure | 450 | 295 | 4.76 | 2.1156 |  | 200 | 45 | 0 | 0 | FO |  |  |  | 0 | 6.7417 | 26.1073 | 2013 | 3 | 12
2013-03-22 18:24 | 2013-03-22 19:13 |  | Y | Y | Commutation failure at Ballycronan more (NI Ice Storm) | 450 | 295 | 0.83 | 0.36889 |  | 200 | 45 | 0 | 0 | FO |  |  |  | 0 | 7.1106 | 26.1073 | 2013 | 3 | 12
2013-03-22 19:31 | 2013-03-22 21:10 |  | Y | Y | Commutation failure at Ballycronan more (NI Ice Storm) | 450 | 295 | 1.65 | 0.73333 |  | 200 | 45 | 0 | 0 | FO | 0 | 7.8439 | 26.1073 | 0 | 7.8439 | 26.1073 | 2013 | 3 | 12
2013-04-23 21:08 | 2013-04-24 00:09 |  | Y | Y | Coylton Line outage (protection failure) Pole 1 trip | 410 | 295 | 3.0178 | 1.8401 |  | 250 | 250 | 0 | 0 | FO |  |  |  | 0 | 1.8401 | 0 | 2013 | 4 | 1
2013-04-01 | 2013-04-30 23:59 |  |  | Y | Pole 2 Cable Fault | 410 | 295 | 719.9833 | 280.9691 |  | 160 | 45 | 250 | 250 | FO |  |  |  | 0 | 282.8092 | 0 | 2013 | 4 | 1
2013-05-01 | 2013-08-31 23:59 |  |  | Y | Pole 2 Cable Fault | 410 | 287 | 2951.9833 | 1151.9935 |  | 160 | 37 | 250 | 250 | FO |  |  |  | 0 | 1434.8027 | 0 | 2013 | 5 | 2
2013-08-12 08:00 | 2013-09-20 06:00 |  | Y | Y | Reconfiguration of Coylton Substation - Stage 1b - Requires S10 & s20 oos | 410 | 287 | 934 | 569.5122 |  | 250 | 250 | 0 | 0 | PO |  |  |  | 0 | 1434.8027 | 569.5122 | 2013 | 8 | 5
2013-09-01 | 2013-11-01 06:00 |  |  | Y | Pole 2 Cable Fault | 410 | 295 | 1470 | 573.6585 |  | 160 | 45 | 250 | 250 | FO |  |  |  | 0 | 2008.4612 | 569.5122 | 2013 | 9 | 6
2013-11-01 06:00 | 2014-03-31 06:00 |  |  | Y | Pole 2 Cable Fault | 450 | 295 | 3600 | 1600 |  | 200 | 45 | 250 | 250 | FO |  |  |  | 0 | 3608.4612 | 569.5122 | 2013 | 11 | 8
2014-03-31 06:00 | 2014-05-01 06:00 |  |  | Y | Pole 2 Cable Fault | 410 | 295 | 744 | 290.3415 |  | 160 | 45 | 250 | 250 | FO | 0 | 3898.8027 | 569.5122 | 0 | 3898.8027 | 569.5122 | 2014 | 3 | 12
2014-05-01 06:00 | 2013-08-31 23:59 |  |  | Y | Pole 2 Cable Fault | 410 | 287 | -5814.0167 | -2268.8846 |  | 160 | 37 | 250 | 250 | FO |  |  |  | 0 | -2268.8846 | 0 | 2014 | 5 | 2
2014-09-01 | 2014-11-01 06:00 |  |  | Y | Pole 2 Cable Fault | 410 | 295 | 1470 | 573.6585 |  | 160 | 45 | 250 | 250 | FO |  |  |  | 0 | -1695.226 | 0 | 2014 | 9 | 6
2014-11-01 06:00 | 2015-04-01 06:00 |  |  | Y | Pole 2 Cable Fault | 450 | 295 | 3624 | 1610.6667 |  | 200 | 45 | 250 | 250 | FO | 0 | -84.5593 | 0 | 0 | -84.5593 | 0 | 2014 | 11 | 8
2015-04-01 06:00 | 2015-05-01 06:00 |  |  | Y | Pole 2 Cable Fault | 410 | 295 | 720 | 280.9756 |  | 160 | 45 | 250 | 250 | FO |  |  |  | 0 | 280.9756 | 0 | 2015 | 4 | 1
2015-05-01 06:00 | 2015-09-01 06:00 |  |  | Y | Pole 2 Cable Fault | 410 | 287 | 2952 | 1152 |  | 160 | 37 | 250 | 250 | FO |  |  |  | 0 | 1432.9756 | 0 | 2015 | 5 | 2
2015-09-01 06:00 | 2015-11-01 06:00 |  |  | Y | Pole 2 Cable Fault | 410 | 295 | 1464 | 571.3171 |  | 160 | 45 | 250 | 250 | FO |  |  |  | 0 | 2004.2927 | 0 | 2015 | 9 | 6
2015-11-01 06:00 | 2016-01-28 06:00 |  |  | Y | Pole 2 Cable Fault | 450 | 295 | 2112 | 938.6667 |  | 200 | 45 | 250 | 250 | FO | 0 | 2942.9593 | 0 | 0 | 2942.9593 | 0 | 2015 | 11 | 8
2014-05-12 22:00 | 2014-05-13 07:00 |  | Y |  | Moyle reconfiguration Testing | 410 | 287 | 9 | 5.4878 |  | 250 | 250 | 0 | 0 | FO |  |  |  | 0 | 5.4878 | 0 | 2014 | 5 | 2
2014-05-14 05:53 | 2014-05-14 08:22 |  | Y |  | Protection trip on return to service in reconfigured mode | 410 | 287 | 2.4833 | 1.5142 |  | 250 | 250 | 0 | 0 | FO |  |  |  | 0 | 7.002 | 0 | 2014 | 5 | 2
2014-05-18 06:00 | 2014-05-18 14:00 |  | Y |  | Moyle reconfiguration Testing | 410 | 287 | 8 | 4.878 |  | 250 | 250 | 0 | 0 | PO |  |  |  | 0 | 7.002 | 4.878 | 2014 | 5 | 2
2014-03-31 07:30 | 2014-04-07 15:30 |  | Y | Y | Reconfiguration on Coylton Substation - Stage 2b - Decommission S10 | 410 | 295 | 176 | 107.3171 |  | 250 | 250 | 0 | 0 | PO | 0 | 7.002 | 112.1951 | 0 | 7.002 | 112.1951 | 2014 | 3 | 12
2014-06-29 05:24 | 2014-06-29 13:58 |  | Y | Y | Low SF6 gas pressure alarm on Coylton line circuit breaker | 410 | 287 | 8.5667 | 5.2236 |  | 250 | 250 | 0 | 0 | FO |  |  |  | 0 | 5.2236 | 0 | 2014 | 6 | 3
2014-07-05 08:30 | 2014-08-29 16:30 |  | Y | Y | Reconfiguration on Coylton Substation - Stage 3a | 410 | 287 | 1328 | 809.7561 |  | 250 | 250 | 0 | 0 | PO |  |  |  | 0 | 5.2236 | 809.7561 | 2014 | 7 | 4
2014-11-03 08:30 | 2014-11-04 16:30 |  | Y | Y | Reconfiguration on Coylton Substation | 410 | 287 | 32 | 19.5122 |  | 250 | 250 | 0 | 0 | PO |  |  |  | 0 | 5.2236 | 829.2683 | 2014 | 11 | 8
2014-12-08 06:35 | 2014-12-08 08:28 |  | Y | Y | Scottish Power 11kV LV incomer failure tripped pole system and standby generator did not operate to restore LV AC supply | 450 | 287 | 1.8833 | 1.0463 | 154 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 5.2236 | 829.2683 | 2014 | 12 | 9
2014-12-10 15:35 | 2014-12-10 16:26 |  | Y | Y | System disturbance on Scottish Power system | 450 | 287 | 0.85 | 0.47222 | 128 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 5.2236 | 829.2683 | 2014 | 12 | 9
2014-12-11 01:37 | 2014-12-11 02:49 |  | Y | Y | Fault on Scottish Power system Coylton line | 450 | 287 | 1.2 | 0.66667 | 200 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 5.2236 | 829.2683 | 2014 | 12 | 9
2014-12-12 09:01 | 2014-12-12 09:26 |  | Y | Y | Scottish Power 11kV LV incomer failure tripped pole system and standby generator did not operate to restore LV AC supply | 450 | 287 | 0.41667 | 0.23148 | 170 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 5.2236 | 829.2683 | 2014 | 12 | 9
2015-03-03 11:15 | 2015-03-04 22:00 |  | Y | Y | Insulator failure on Scottish Power Coylton circuit | 450 | 287 | 34.75 | 19.3056 | 165.28 | 250 | 250 | 0 | 0 |  | 0 | 5.2236 | 829.2683 | 0 | 5.2236 | 829.2683 | 2015 | 3 | 12
2015-06-04 05:48 | 2015-06-04 07:17 |  | Y | Y | Pole control software malfunction | 450 | 287 | 1.4833 | 0.82407 | 23 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2015 | 6 | 3
2015-08-07 11:42 | 2015-08-07 13:08 |  | Y | Y | Power outage on Coylton circuit | 410 | 287 | 1.4417 | 0.87907 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2015 | 8 | 5
2015-09-26 07:00 | 2015-09-26 19:00 |  | Y | Y | Power outage on pole 1 to faciltate installation of replacemnent cable pole 2 | 410 | 295 | 12 | 7.3171 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2015 | 9 | 6
2015-09-27 07:00 | 2015-09-27 19:00 |  | Y | Y | Power outage on pole 1 to faciltate installation of replacemnent cable pole 2 | 410 | 295 | 12 | 7.3171 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2015 | 9 | 6
2015-10-02 07:20 | 2015-10-02 08:50 |  | Y | Y | Pole out of sequence with transformer tap changer | 410 | 295 | 1.5089 | 0.92005 | 68 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2015 | 10 | 7
2015-11-06 23:00 | 2015-11-07 07:00 |  | Y | Y | Outage required to allow Nexans (as part of current EPC contract to lay new MRC cables) to trench the new MRC which is at one point in close vicinity of the existing South IRC | 450 | 295 | 8 | 4.4444 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2015 | 11 | 8
2015-12-09 06:00 | 2015-12-10 07:00 |  | Y |  | Outage required to enable rock placement on live Pole 1 cable as per requirements of EPC contract (Nexans) | 450 | 295 | 25 | 13.8889 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2015 | 12 | 9
2015-12-11 15:00 | 2015-12-14 05:00 |  | Y |  | Outage required to enable rock placement on live Pole 1 cable as per requirements of EPC contract (Nexans) | 450 | 295 | 62 | 34.4444 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2015 | 12 | 9
2016-01-30 08:30 | 2016-01-30 16:30 |  | Y | Y | Scottish Power outage on Auchencrosh-Mark Hill-Coylton 275kV circuit | 450 | 295 | 8 | 4.4444 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2016 | 1 | 10
2016-01-31 08:30 | 2016-01-31 16:30 |  | Y | Y | Scottish Power outage on Auchencrosh-Mark Hill-Coylton 275kV circuit | 450 | 295 | 8 | 4.4444 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2016 | 1 | 10
2016-01-21 10:30 | 2016-01-21 16:30 |  | Y | Y | Category A Testing Following Recent MRC Cable Installation | 450 | 295 | 6 | 3.3333 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2016 | 1 | 10
2016-01-22 11:00 | 2016-01-22 13:00 |  | Y | Y | Category A Testing Following Recent MRC Cable Installation | 450 | 295 | 2 | 1.0444 | 0 | 235 | 235 | 15 | 15 |  |  |  |  | 0 | 0 | 0 | 2016 | 1 | 10
2016-02-22 07:00 | 2016-02-22 09:00 |  | N | Y | End of Category B testing of Pole 2 to allow takeover of Section 1 Works of MRC project | 450 | 295 | 2 | 0.88889 | 0 | 200 | 45 | 250 | 250 |  |  |  |  | 0 | 0 | 0 | 2016 | 2 | 11
2016-03-29 06:00 | 2016-03-31 23:59 |  | Y | N | Outage to enable connection of Pole 1 of the Moyle Interconnector to new MRC cable in line with MRC Project Works | 450 | 295 | 65.9833 | 29.3259 | 0 | 200 | 45 | 250 | 250 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2016 | 3 | 12
2016-04-01 | 2016-06-06 08:30 |  | Y | N | Outage to enable connection of Pole 1 of the Moyle Interconnector to new MRC cable in line with MRC Project Works | 410 | 295 | 1592.5 | 621.4634 | 0 | 160 | 45 | 250 | 250 |  |  |  |  | 0 | 0 | 0 | 2016 | 4 | 1
2016-06-06 08:30 | 2016-09-16 16:30 |  | Y | Y | National Grid Outage to Re-String the Coylton 275kV transmission line | 410 | 287 | 2456 | 2456 | 0 | 410 | 287 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 2016 | 6 | 3
2016-04-13 10:00 | 2016-04-15 12:34 |  | Y | Y | Outage to enable joint bay reinforcement for Pole 1 cable repair works | 410 | 295 | 50.5667 | 30.8333 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2016 | 4 | 1
2016-04-26 06:00 | 2016-04-28 20:00 |  | Y | Y | Outage on Pole 2 to carry out rock breaking to enable Pole 1 jointing works to commence | 410 | 295 | 62 | 37.8049 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2016 | 4 | 1
2016-05-06 18:30 | 2016-05-06 19:30 |  | Y | Y | Short Outage on Pole 2 to carry out emergency valve cooling control card replacement following failure | 410 | 287 | 1 | 0.60976 | 0 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2016 | 5 | 2
2016-09-16 16:30 | 2016-09-17 06:00 |  | Y | Y | Moyle testing following cable repairs and National Grid Outage to Re-String the Coylton 275kV transmission line | 410 | 295 | 13.5 | 13.5 | 0 | 410 | 287 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2016 | 9 | 6
2016-09-17 06:00 | 2016-09-21 06:00 |  | Y | Y | Moyle testing following cable repairs and National Grid Outage to Re-String the Coylton 275kV transmission line | 410 | 295 | 96 | 37.4634 | 0 | 160 | 45 | 250 | 250 |  |  |  |  | 0 | 0 | 0 | 2016 | 9 | 6
2016-09-22 16:09 | 2016-09-22 17:06 | 2016-09-24 16:09 | N | Y | Cooling water pump failure pole 2 Auchencrosh - broken seals leading to loss of water and reduced water level | 410 | 295 | 0.95611 | 0.37312 | 45 | 160 | 45 | 250 | 250 |  |  |  |  | 0 | 0 | 0 | 2016 | 9 | 6
2016-09-29 18:53 | 2016-09-29 21:03 |  | N | Y | Pole 2 valve cooling pump seals leak leading to low level water trip | 410 | 295 | 2.1561 | 0.84141 | 45 | 160 | 45 | 250 | 250 |  |  |  |  | 0 | 0 | 0 | 2016 | 9 | 6
2016-11-07 19:46 | 2016-11-07 21:29 |  | N | Y | Pole 2 Commutation Failure | 450 | 295 | 1.7225 | 0.76556 | 22 | 200 | 45 | 250 | 250 |  |  |  |  | 0 | 0 | 0 | 2016 | 11 | 8
2017-02-18 15:25 | 2017-09-27 06:00 |  | Y | N | Cable fault south cable pole 1 | 450 | 295 | 5294.5833 | 1882.5185 | 0 | 160 | 45 | 250 | 250 |  |  |  |  | 0 | 0 | 0 | 2017 | 2 | 11
2017-02-23 11:32 | 2017-02-24 01:07 |  | Y | Y | Scottish Power outage on Auchencrosh-Mark Hill-Coylton 275kV circuit | 450 | 295 | 13.5769 | 7.5427 | 250 | 250 | 250 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 2017 | 2 | 11
2017-03-21 05:05 | 2017-03-21 06:56 |  | N | Y | Pole tripped due on dc overvoltage protection | 450 | 295 | 1.85 | 1.0278 | 196 | 250 | 250 | 250 | 250 | FO |  |  |  | 0 | 1.0278 | 0 | 2017 | 3 | 12
2017-03-21 12:15 | 2017-03-22 13:14 |  | N | Y | Pole tripped again on dc overvoltage protection. On investigation proved to be a failure of a primary voltage measurement instrument. | 450 | 295 | 24.9833 | 13.8796 | 248 | 250 | 250 | 250 | 250 | FO | 0 | 14.9074 | 0 | 0 | 14.9074 | 0 | 2017 | 3 | 12
2017-05-13 07:30 | 2017-05-13 08:56 |  | N | Y | Line fault on the Scottish Power Coylton Auchencrosh circuit | 410 | 287 | 1.4333 | 0.87398 | 247 | 250 | 250 | 250 | 250 | FO |  |  |  | 0 | 0.87398 | 0 | 2017 | 5 | 2
2017-06-02 07:00 | 2017-06-02 13:00 |  | N | Y | Scheduled outage on pole 2 to carry out maintenance on the combined cable system | 410 | 287 | 6 | 3.6585 | 0 | 250 | 250 | 0 | 0 | SO |  |  |  | 3.6585 | 0.87398 | 0 | 2017 | 6 | 3
2017-07-14 10:42 | 2017-07-14 11:11 |  | N | Y | Pole 2 tripped due to failure of a MCB on ac station interface | 410 | 287 | 0.48306 | 0.29455 | 71 | 250 | 250 | 250 | 250 | FO |  |  |  | 3.6585 | 1.1685 | 0 | 2017 | 7 | 4
2017-08-22 17:33 | 2017-08-22 17:54 |  | N | Y | Earth fault on AC transmission network in Northern Ireland | 410 | 287 | 0.35222 | 0.21477 | 31 | 250 | 250 | 0 | 0 | FO |  |  |  | 3.6585 | 1.3833 | 0 | 2017 | 8 | 5
2017-08-23 00:44 | 2017-08-23 03:02 |  | N | Y | Pole trip caused by loss of LV power supply to Ballycronan More converter station due to distibution network disturbance | 410 | 287 | 2.3044 | 1.4051 | 250 | 250 | 250 | 0 | 0 | FO |  |  |  | 3.6585 | 2.7884 | 0 | 2017 | 8 | 5
2017-09-23 13:00 | 2017-09-23 15:00 |  | N | Y | Scheduled outage on pole 2 to carry out maintenance on the combined cable system ahead of pole 1 return to service | 410 | 295 | 2 | 1.2195 | 0 | 250 | 250 | 0 | 0 | SO |  |  |  | 4.878 | 2.7884 | 0 | 2017 | 9 | 6
2017-10-17 01:27 | 2017-10-17 05:36 |  | N | Y | Pole 2 trip - UPS undervoltage fault | 450 | 295 | 4.15 | 1.8444 | 52.5 | 200 | 57.5 | 250 | 237.5 | FO |  |  |  | 4.878 | 4.6329 | 0 | 2017 | 10 | 7
2017-12-29 09:10 | 2017-12-29 09:28 |  | N | Y | Trip during investigative works for scheduled outage later that day | 450 | 80 | 0.31167 | 0.11081 | 0 | 160 | 0 | 250 | 237.5 | FO |  |  |  | 4.878 | 4.7437 | 0 | 2017 | 12 | 9
2017-12-29 11:41 | 2017-12-29 14:27 |  | N | Y | Scheduled outage to enable access to valve hall to replace failed thryristors | 450 | 80 | 2.7561 | 0.97995 | 0 | 160 | 0 | 250 | 237.5 | SO |  |  |  | 5.858 | 4.7437 | 0 | 2017 | 12 | 9
2018-01-12 09:00 | 2018-01-12 13:56 |  | Y | N | Scheduled outage to carry out replacement of data acquisition unit on converter transformer | 450 | 80 | 4.9333 | 2.1926 | 0 | 200 | 0 | 250 | 237.5 | SO |  |  |  | 8.0506 | 4.7437 | 0 | 2018 | 1 | 10
2018-01-24 16:22 | 2018-01-24 16:46 |  | N | Y | Pole 2 failed to deblock due to conductivity sensor | 450 | 80 | 0.4 | 0.17778 | 0 | 200 | 0 | 250 | 237.5 | FO |  |  |  | 8.0506 | 4.9215 | 0 | 2018 | 1 | 10
2018-03-18 11:52 | 2018-03-18 23:20 |  | N | Y | Pole 2 trip due to valve cooling flow sensor failure | 450 | 80 | 11.4581 | 5.0925 | 0 | 200 | 0 | 250 | 237.5 | FO | 8.0506 | 10.014 | 0 | 8.0506 | 10.014 | 0 | 2018 | 3 | 12
2018-06-20 06:00 | 2018-06-22 06:00 |  | N | Y | Biennial planned outage pole 2 | 410 | 80 | 48 | 18.7317 | 0 | 160 | 0 | 250 | 237.5 | PO |  |  |  | 0 | 0 | 18.7317 | 2018 | 6 | 3
2018-08-09 10:00 | 2018-08-09 14:00 |  | Y | Y | Outage on Scottish Transmission System | 410 | 80 | 4 | 4 | 0 | 410 | 80 | 0 | 0 | PO | 0 | 0 | 22.7317 | 0 | 0 | 22.7317 | 2018 | 8 | 5
Formulas:
End date = [Start date]+([Outage duration]/24)
Start date = [End date, row above]

## Sheet1 (hidden)
1000 |  | 19600
12000 |  | 12000
13000 |  | 31600
2016-10-31
2015-12-31 | 305 |  | 365
| 3660000 |  | 4380000
| 3647000 |  | 4348400
| 99.64% |  | 99.28%

## Sense check
2016-08-31 06:00
Month ending | time axis 2009-12-31 to 2018-05-31
| Max import |  | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410
| One pole outage duration in month (hrs) |  | 8.65 | 0.68 | 4.63 | 0 | 0 | 0 | 0 | 0 | 491.3167 | 744 | 428.83 | 0 | 0 | 0 | 1.7 | 0 | 1.02 | 91.7167 | 744 | 590 | 0 | 0 | 0 | 0 | 291 | 462 | 0 | 0 | 0 | 157.7167 | 744 | 742.9525 | 707.7667 | 743 | 672 | 744 | 696 | 672 | 728.6664 | 716.9822 | 744 | 720 | 744 | 296 | 234 | 744 | 720 | 744 | 744 | 672 | 568 | 720 | 724.5167 | 711.4333 | 128.5 | 31.5 | 720 | 744 | 688 | 739.65 | 744 | 672 | 709.25 | 720 | 744 | 718.5167 | 744 | 742.5583 | 696 | 742.4911 | 712 | 657 | 624 | 2 | 65.9833 | 607.4333 | 743 | 144 | 0 | 0 | 3.1122 | 0 | 1.7225 | 0 | 0 | 211.0064 | 717.1667 | 720 | 742.5667 | 714 | 743.5169 | 741.3433 | 628 | 4.15 | 0 | 3.0678 | 5.3333 | 0 | 11.4581 | 0 | 0
| Both pole outage duration in month (hrs) |  | 0 | 0 | 0 | 0 | 0 | 384 | 192 | 0 | 0 | 0 | 3.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 720 | 744 | 720 | 744 | 453 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0475 | 12.2333 | 1 | 48 |  | 48 |  | 15.3336 | 3.0178 |  |  |  | 448 | 486 | [5 empty] | 176 |  | 19.4833 | 8.5667 | 615.5 | 712.5 | 0 | 0 | 32 | 4.35 | 0 | 0 | 34.75 | 0 | 0 | 1.4833 | 0 | 1.4417 | 24 | 1.5089 | 8 | 87 | 24 | 0 | 0 | 112.5667 | 1 | 576 | 744 | 744 | 504 | 0 | 0 | 0 | 0 | 13.5769 | 26.8333 | 0 | 1.4333 | 6 | 0.48306 | 2.6567 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unavailable |  | 8.65 | 0.68 | 4.63 | 0 | 0 | 384 | 192 | 0 | 491.3167 | 744 | 432 | 0 | 0 | 0 | 1.7 | 0 | 1.02 | 91.7167 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 462 | 0 | 0 | 0 | 157.7167 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 648 | 2 | 65.9833 | 720 | 744 | 720 | 744 | 744 | 507.1122 | 0 | 1.7225 | 0 | 0 | 224.5833 | 744 | 720 | 744 | 720 | 744 | 744 | 630 | 4.15 | 0 | 3.0678 | 5.3333 | 0 | 11.4581 | 0 | 0
[22 empty] | 6 | pole maintenance
Calculation based on connection limits |  | 2016-10-31: connection limits used for 16/17 targets (i.e. 50% when one cable off)
| Max availability (MWh) |  | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 313200 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 313200 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040
| One pole unavailability |  | -1730 | -136 | -926 | 0 | 0 | 0 | 0 | 0 | -78610.6667 | -119040 | -85766 | 0 | 0 | 0 | -340 | 0 | -163.2 | -14674.6667 | -119040 | -94400 | 0 | 0 | 0 | 0 | -58200 | -92400 | 0 | 0 | 0 | -25234.6667 | -119040 | -118872.4 | -113242.6667 | -118880 | -134400 | -148800 | -139200 | -134400 | -145733.2778 | -114717.1556 | -119040 | -115200 | -119040 | -47360 | -37440 | -119040 | -144000 | -148800 | -148800 | -134400 | -113600 | -115200 | -115922.6667 | -113829.3333 | -20560 | -5040 | -115200 | -119040 | -137600 | -147930 | -148800 | -134400 | -141850 | -115200 | -119040 | -114962.6667 | -119040 | -118809.3333 | -111360 | -118798.5778 | -142400 | -131400 | -124800 | -400 | -13196.6667 | -97189.3333 | -118880 | -23040 | 0 | 0 | -497.9556 | 0 | -344.5 | 0 | 0 | -42201.2778 | -143433.3333 | -115200 | -118810.6667 | -114240 | -118962.7111 | -118614.9333 | -100480 | -664 | 0 | -613.5556 | -1066.6667 | 0 | -2291.6111 | 0 | 0
| Two pole unavailability |  | 0 | 0 | 0 | 0 | 0 | -157440 | -78720 | 0 | 0 | 0 | -1426.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -63140 | -295200 | -305040 | -324000 | -334800 | -203850 | 0 | 0 | 0 | 0 | 0 | 0 | -429.475 | -5015.6667 | -410 | -21600 | 0 | -21600 | 0 | -6900.125 | -1237.2889 | 0 | 0 | 0 | -183680 | -199260 | 0 | 0 | 0 | 0 | 0 | -79200 | 0 | -7988.1667 | -3512.3333 | -252355 | -292125 | 0 | 0 | -14400 | -1957.5 | 0 | 0 | -15637.5 | 0 | 0 | -608.1667 | 0 | -591.0833 | -9840 | -618.6444 | -3600 | -39150 | -10800 | 0 | 0 | -46152.3333 | -410 | -236160 | -305040 | -305040 | -206640 | 0 | 0 | 0 | 0 | -6109.625 | -12075 | 0 | -587.6667 | -2460 | -198.0528 | -1089.2333 | -820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Availability |  | 333070 | 302264 | 333874 | 295200 | 305040 | 137760 | 226320 | 305040 | 216589.3333 | 186000 | 236807.5 | 334800 | 334800 | 302400 | 334460 | 295200 | 304876.8 | 280525.3333 | 186000 | 147500 | 0 | 0 | 0 | 0 | 72750 | 220800 | 334800 | 295200 | 305040 | 269965.3333 | 186000 | 185738.125 | 176941.6667 | 185750 | 168000 | 186000 | 174000 | 168000 | 182166.5972 | 179245.5556 | 186000 | 180000 | 186000 | 74000 | 58500 | 186000 | 180000 | 186000 | 186000 | 168000 | 142000 | 180000 | 181129.1667 | 177858.3333 | 32125 | 7875 | 180000 | 186000 | 172000 | 184912.5 | 186000 | 168000 | 177312.5 | 180000 | 186000 | 179629.1667 | 186000 | 185639.5833 | 174000 | 185622.7778 | 178000 | 164250 | 199200 | 312800 | 321603.3333 | 151858.3333 | 185750 | 36000 | 0 | 0 | 88062.0444 | 305040 | 323655.5 | 334800 | 334800 | 254089.0972 | 179291.6667 | 180000 | 185641.6667 | 178500 | 185879.2361 | 185335.8333 | 193900 | 304376 | 324000 | 334186.4444 | 333733.3333 | 302400 | 332508.3889 | 295200 | 305040
[54 empty] | 60.98% | 59.38% | 60.25% | 10.53% | 2.582% | 60.98% | 60.98% | 53.09% | 55.23% | 55.56% | 55.56% | 52.96% | 60.98% | 60.98% | 60.85% | 60.98% | 60.86% | 58.94% | 60.85% | 54.94% | 49.06% | 59.5% | 99.87% | 96.06% | 51.44% | 60.89% | 12.2% | 0% | 0% | 29.83% | 100% | 99.89% | 100% | 100% | 84.02% | 53.55% | 60.98% | 60.86% | 60.47% | 60.94% | 60.76% | 65.68% | 99.78% | 100% | 99.82% | 99.68% | 100% | 99.32% | 100% | 100%
| Rolling 12 month average availability | [12 empty] | 85.98% | 86.03% | 86.03% | 86.05% | 86.05% | 86.04% | 89.86% | 88.78% | 84.57% | 78.77% | 73.79% | 67.46% | 58.5% | 51.48% | 49.16% | 49.17% | 49.17% | 49.17% | 48.89% | 48.89% | 49.91% | 54.63% | 59.59% | 64.07% | 69.03% | 71.74% | 70.53% | 66.45% | 63.34% | 60.16% | 57.75% | 57.75% | 54.76% | 51.59% | 51.6% | 51.92% | 51.92% | 52.24% | 52.24% | 51.16% | 51.18% | 51.05% | 51% | 46.88% | 45.11% | 48.36% | 48.36% | 48.15% | 48.12% | 48.12% | 48.12% | 49.06% | 49.06% | 49.19% | 49.24% | 53.36% | 58.11% | 57.95% | 57.94% | 58.1% | 57.55% | 57.9% | 61.6% | 65.45% | 64.7% | 64.69% | 60.86% | 55.9% | 50.94% | 48.65% | 51.84% | 55.73% | 60.28% | 63.89% | 62.51% | 58.7% | 59.45% | 59.45% | 63.26% | 68.24% | 73.2% | 76.03% | 76.01% | 76.02% | 76.01% | 75.98% | 77.27% | 81.37% | 84.45% | 87.65%
[71 empty] | 60.6% | [5 empty] | 34.55% | [5 empty] | 25.64%
42.31%
Calculation based on technical capacity
| Max availability (MWh) |  | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 348000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 348000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000
| One pole unavailability |  | -2162.5 | -170 | -1157.5 | 0 | 0 | 0 | 0 | 0 | -122829.1667 | -186000 | -107207.5 | 0 | 0 | 0 | -425 | 0 | -255 | -22929.1667 | -186000 | -147500 | 0 | 0 | 0 | 0 | -72750 | -115500 | 0 | 0 | 0 | -39429.1667 | -186000 | -185738.125 | -176941.6667 | -185750 | -168000 | -186000 | -174000 | -168000 | -182166.5972 | -179245.5556 | -186000 | -180000 | -186000 | -74000 | -58500 | -186000 | -180000 | -186000 | -186000 | -168000 | -142000 | -180000 | -181129.1667 | -177858.3333 | -32125 | -7875 | -180000 | -186000 | -172000 | -184912.5 | -186000 | -168000 | -177312.5 | -180000 | -186000 | -179629.1667 | -186000 | -185639.5833 | -174000 | -185622.7778 | -178000 | -164250 | -156000 | -500 | -16495.8333 | -151858.3333 | -185750 | -36000 | 0 | 0 | -778.0556 | 0 | -430.625 | 0 | 0 | -52751.5972 | -179291.6667 | -180000 | -185641.6667 | -178500 | -185879.2361 | -185335.8333 | -157000 | -1037.5 | 0 | -766.9444 | -1333.3333 | 0 | -2864.5139 | 0 | 0
| Two pole unavailability |  | 0 | 0 | 0 | 0 | 0 | -192000 | -96000 | 0 | 0 | 0 | -1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -77000 | -360000 | -372000 | -360000 | -372000 | -226500 | 0 | 0 | 0 | 0 | 0 | 0 | -523.75 | -6116.6667 | -500 | -24000 | 0 | -24000 | 0 | -7666.8056 | -1508.8889 | 0 | 0 | 0 | -224000 | -243000 | 0 | 0 | 0 | 0 | 0 | -88000 | 0 | -9741.6667 | -4283.3333 | -307750 | -356250 | 0 | 0 | -16000 | -2175 | 0 | 0 | -17375 | 0 | 0 | -741.6667 | 0 | -720.8333 | -12000 | -754.4444 | -4000 | -43500 | -12000 | 0 | 0 | -56283.3333 | -500 | -288000 | -372000 | -372000 | -252000 | 0 | 0 | 0 | 0 | -6788.4722 | -13416.6667 | 0 | -716.6667 | -3000 | -241.5278 | -1328.3333 | -1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Availability |  | 369837.5 | 335830 | 370842.5 | 360000 | 372000 | 168000 | 276000 | 372000 | 237170.8333 | 186000 | 251207.5 | 372000 | 372000 | 336000 | 371575 | 360000 | 371745 | 337070.8333 | 186000 | 147500 | 0 | 0 | 0 | 0 | 72750 | 232500 | 372000 | 360000 | 372000 | 320570.8333 | 186000 | 185738.125 | 176941.6667 | 185750 | 168000 | 186000 | 174000 | 168000 | 182166.5972 | 179245.5556 | 186000 | 180000 | 186000 | 74000 | 58500 | 186000 | 180000 | 186000 | 186000 | 168000 | 142000 | 180000 | 181129.1667 | 177858.3333 | 32125 | 7875 | 180000 | 186000 | 172000 | 184912.5 | 186000 | 168000 | 177312.5 | 180000 | 186000 | 179629.1667 | 186000 | 185639.5833 | 174000 | 185622.7778 | 178000 | 164250 | 204000 | 347500 | 355504.1667 | 151858.3333 | 185750 | 36000 | 0 | 0 | 107221.9444 | 372000 | 359569.375 | 372000 | 372000 | 276459.9306 | 179291.6667 | 180000 | 185641.6667 | 178500 | 185879.2361 | 185335.8333 | 202000 | 370962.5 | 360000 | 371233.0556 | 370666.6667 | 336000 | 369135.4861 | 360000 | 372000
| Rolling 12 month average availability | [12 empty] | 83.81% | 83.86% | 83.86% | 83.88% | 83.88% | 83.87% | 87.73% | 85.68% | 80.55% | 75.14% | 70.89% | 65.16% | 56.66% | 49.83% | 47.34% | 47.35% | 47.35% | 47.35% | 46.98% | 46.98% | 47.85% | 51.88% | 56.11% | 59.93% | 64.17% | 66.47% | 65.18% | 60.85% | 56.72% | 52.48% | 49.27% | 49.27% | 46.71% | 44.01% | 44.02% | 44.29% | 44.29% | 44.56% | 44.56% | 43.65% | 43.66% | 43.55% | 43.5% | 39.99% | 38.48% | 41.26% | 41.26% | 41.07% | 41.05% | 41.05% | 41.05% | 41.85% | 41.85% | 41.97% | 42.01% | 45.52% | 49.58% | 49.44% | 49.43% | 49.57% | 49.1% | 49.51% | 53.46% | 57.52% | 56.88% | 56.87% | 53.6% | 49.37% | 45.14% | 43.62% | 47.86% | 52% | 56.73% | 60.55% | 59.1% | 55.07% | 55.71% | 55.71% | 58.97% | 63.21% | 67.44% | 69.6% | 69.58% | 69.59% | 69.57% | 69.54% | 70.9% | 75.24% | 79.35% | 83.6%
[71 empty] | 49.69% | [5 empty] | 42.48% | [5 empty] | 21.9%
44.06%
Month ending | time axis 2009-12-31 to 2018-05-31
| Max import |  | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 410 | 410 | 410 | 410 | 450 | 450 | 450 | 450 | 450 | 410 | 410
Excludes pole 2 cable outage only not any other related outages!
| Cable fault and NG outage durations - 1 pole |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 491.3167 | 744 | 428.83 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7167 | 744 | 590 |  |  |  |  | 291 | 462 |  |  |  | 157.7167 | 744 | 742.9525 | 707.7667 | 743 | 672 | 744 | 696 | 672 | 728.6664 | 716.9822 | 744 | 720 | 744 | 296 | 234 | 744 | 720 | 744 | 744 | 672 | 568 | 720 | 724.5167 | 711.4333 | 128.5 | 31.5 | 720 | 744 | 688 | 739.65 | 744 | 672 | 709.25 | 720 | 744 | 718.5167 | 744 | 742.5583 | 696 | 742.4911 | 712 | 657 | 624 | 2 | 65.9833 | 607.4333 | 743 | 144 | 0 | 0 | 3.1122 | 0 | 1.7225 | 0 | 0 | 211.0064 | 717.1667 | 720 | 742.5667 | 714 | 743.5169 | 741.3433 | 628 | 4.15 | 0 | 3.0678 | 5.3333 | 0 | 11.4581 | 0 | 0
| Cable fault and NG outage durations - 2 pole | 2010-01-31: 0; 2010-02-28: 0; 2010-03-31: 0; 2010-04-30: 0; 2010-05-31: 0; 2010-06-30: 384; 2010-07-31: 192; 2010-08-31: 0; 2010-09-30: 0; 2010-10-31: 0; 2010-11-30: 0; 2010-12-31: 0; 2011-01-31: 0; 2011-02-28: 0; 2011-03-31: 0; 2011-04-30: 0; 2011-05-31: 0; 2011-06-30: 0; 2011-07-31: 0; 2011-08-31: 154; 2011-09-30: 720; 2011-10-31: 744; 2011-11-30: 720; 2011-12-31: 744; 2012-01-31: 453; 2013-08-31: 448; 2013-09-30: 486; 2014-03-31: 176; 2014-07-31: 615.5; 2014-08-31: 712.5; 2014-11-30: 32; 2015-03-31: 34.75; 2015-08-31: 1.4417; 2016-01-31: 16; 2016-04-30: 112.5667; 2016-05-31: 0; 2016-06-30: 576; 2016-07-31: 744; 2016-08-31: 744; 2016-09-30: 504; 2016-10-31: 0; 2016-11-30: 0; 2016-12-31: 0; 2017-01-31: 0; 2017-02-28: 13.5769; 2017-03-31: 0; 2017-04-30: 0; 2017-05-31: 1.4333; 2017-06-30: 6; 2017-07-31: 0.48306; 2017-08-31: 2.6567; 2017-09-30: 2; 2017-10-31: 0; 2017-11-30: 0; 2017-12-31: 0; 2018-01-31: 0; 2018-02-28: 0; 2018-03-31: 0; 2018-04-30: 0; 2018-05-31: 0
| Adjusted outages exluding cables and NG - 1 pole |  | 8.65 | 0.68 | 4.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 1.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.15 | 0 | 3.0678 | 5.3333 | 0 | 11.4581 | 0 | 0
| Adjusted outages exluding cables and NG - 2 pole |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0475 | 12.2333 | 1 | 48 | 0 | 48 | 0 | 15.3336 | 3.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4833 | 8.5667 | 0 | 0 | 0 | 0 | 0 | 4.35 | 0 | 0 | 0 | 0 | 0 | 1.4833 | 0 | 0 | 24 | 1.5089 | 8 | 87 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8333 | 0 | 1.4333 | 6 | 0.48306 | 2.6567 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calculation based on connection limits
| Max availability (MWh) |  | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 313200 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 313200 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 305040
| One pole unavailability |  | -1730 | -136 | -926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -340 | 0 | -163.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -344.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -664 | 0 | -613.5556 | -1066.6667 | 0 | -2291.6111 | 0 | 0
| Two pole unavailability |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1426.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -429.475 | -5015.6667 | -410 | -21600 | 0 | -21600 | 0 | -6900.125 | -1237.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7988.1667 | -3512.3333 | 0 | 0 | 0 | 0 | 0 | -1957.5 | 0 | 0 | 0 | 0 | 0 | -608.1667 | 0 | 0 | -9840 | -618.6444 | -3600 | -39150 | -3600 | 0 | 0 | 0 | -410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12075 | 0 | -587.6667 | -2460 | -198.0528 | -1089.2333 | -820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Availability |  | 333070 | 302264 | 333874 | 295200 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 322573.5 | 334800 | 334800 | 302400 | 334460 | 295200 | 304876.8 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 313200 | 334800 | 295200 | 305040 | 295200 | 305040 | 304610.525 | 290184.3333 | 304630 | 302400 | 334800 | 313200 | 302400 | 327899.875 | 293962.7111 | 305040 | 295200 | 305040 | 305040 | 295200 | 305040 | 324000 | 334800 | 334800 | 302400 | 334800 | 295200 | 297051.8333 | 291687.6667 | 305040 | 305040 | 295200 | 305040 | 324000 | 332842.5 | 334800 | 302400 | 334800 | 295200 | 305040 | 294591.8333 | 305040 | 305040 | 285360 | 304421.3556 | 320400 | 295650 | 331200 | 313200 | 334800 | 295200 | 304630 | 295200 | 305040 | 305040 | 295200 | 305040 | 323655.5 | 334800 | 334800 | 302400 | 322725 | 295200 | 304452.3333 | 292740 | 304841.9472 | 303950.7667 | 294380 | 304376 | 324000 | 334186.4444 | 333733.3333 | 302400 | 332508.3889 | 295200 | 305040
[90 empty] | 100% | 99.81% | 99.17% | 99.94% | 99.64% | 99.72% | 99.78% | 100% | 99.82% | 99.68% | 100% | 99.32% | 100% | 100%
| Rolling 12 month average availability | [12 empty] | 99.89% | 99.93% | 99.94% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.99% | 99.99% | 99.99% | 99.99% | 100% | 100% | 100% | 100% | 100% | 99.99% | 99.85% | 99.84% | 99.27% | 99.27% | 98.69% | 98.69% | 98.5% | 98.47% | 98.47% | 98.47% | 98.47% | 98.48% | 98.62% | 98.63% | 99.2% | 99.2% | 99.78% | 99.78% | 99.97% | 100% | 99.79% | 99.69% | 99.69% | 99.69% | 99.69% | 99.69% | 99.69% | 99.64% | 99.64% | 99.64% | 99.64% | 99.64% | 99.85% | 99.93% | 99.93% | 99.93% | 99.67% | 99.65% | 99.56% | 98.56% | 98.46% | 98.47% | 98.47% | 98.47% | 98.46% | 98.47% | 98.47% | 98.47% | 98.74% | 98.75% | 98.84% | 99.88% | 99.98% | 99.98% | 99.66% | 99.66% | 99.65% | 99.59% | 99.58% | 99.55% | 99.53% | 99.51% | 99.52% | 99.5% | 99.48% | 99.48% | 99.74% | 99.74% | 99.75%
0.99977
[8 empty] | 48 | 0.5479% | 2
[14 empty] | 99.8 | 99.5 | 99.5 | 99.6 | 99.7 | [26 empty] | 98.8 | 99.5 | 99.5 | 99.6 | 99.7
Calculation based on technical capacity
| Max availability (MWh) |  | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 348000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 348000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 372000
| One pole unavailability |  | -2162.5 | -170 | -1157.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -425 | 0 | -255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -430.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1037.5 | 0 | -766.9444 | -1333.3333 | 0 | -2864.5139 | 0 | 0
| Two pole unavailability |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -523.75 | -6116.6667 | -500 | -24000 | 0 | -24000 | 0 | -7666.8056 | -1508.8889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9741.6667 | -4283.3333 | 0 | 0 | 0 | 0 | 0 | -2175 | 0 | 0 | 0 | 0 | 0 | -741.6667 | 0 | 0 | -12000 | -754.4444 | -4000 | -43500 | -4000 | 0 | 0 | 0 | -500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13416.6667 | 0 | -716.6667 | -3000 | -241.5278 | -1328.3333 | -1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Availability |  | 369837.5 | 335830 | 370842.5 | 360000 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 358415 | 372000 | 372000 | 336000 | 371575 | 360000 | 371745 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 348000 | 372000 | 360000 | 372000 | 360000 | 372000 | 371476.25 | 353883.3333 | 371500 | 336000 | 372000 | 348000 | 336000 | 364333.1944 | 358491.1111 | 372000 | 360000 | 372000 | 372000 | 360000 | 372000 | 360000 | 372000 | 372000 | 336000 | 372000 | 360000 | 362258.3333 | 355716.6667 | 372000 | 372000 | 360000 | 372000 | 360000 | 369825 | 372000 | 336000 | 372000 | 360000 | 372000 | 359258.3333 | 372000 | 372000 | 348000 | 371245.5556 | 356000 | 328500 | 368000 | 348000 | 372000 | 360000 | 371500 | 360000 | 372000 | 372000 | 360000 | 372000 | 359569.375 | 372000 | 372000 | 336000 | 358583.3333 | 360000 | 371283.3333 | 357000 | 371758.4722 | 370671.6667 | 359000 | 370962.5 | 360000 | 371233.0556 | 370666.6667 | 336000 | 369135.4861 | 360000 | 372000
| Rolling 12 month average availability | [12 empty] | 99.88% | 99.93% | 99.94% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.98% | 99.98% | 99.98% | 99.98% | 99.99% | 99.99% | 100% | 100% | 100% | 99.99% | 99.85% | 99.84% | 99.29% | 99.29% | 98.74% | 98.74% | 98.57% | 98.53% | 98.53% | 98.53% | 98.53% | 98.54% | 98.68% | 98.69% | 99.24% | 99.24% | 99.79% | 99.79% | 99.97% | 100% | 99.78% | 99.68% | 99.68% | 99.68% | 99.68% | 99.68% | 99.68% | 99.63% | 99.63% | 99.63% | 99.63% | 99.63% | 99.85% | 99.93% | 99.93% | 99.93% | 99.66% | 99.64% | 99.55% | 98.61% | 98.52% | 98.52% | 98.52% | 98.52% | 98.51% | 98.53% | 98.53% | 98.53% | 98.8% | 98.82% | 98.9% | 99.89% | 99.98% | 99.98% | 99.67% | 99.67% | 99.67% | 99.6% | 99.59% | 99.56% | 99.54% | 99.52% | 99.53% | 99.51% | 99.48% | 99.48% | 99.72% | 99.72% | 99.74%
Note on CK9: Emma Jayne Armstrong: cable fault outage
Note on CK11: Emma Jayne Armstrong: NG outage
Note on CH54: Emma Jayne Armstrong: commutation failure - not NG or fault related

## Sheet4
|  | Month | 2017-04-30 | 2017-05-31 | 2017-06-30 | 2017-07-31 | 2017-08-31 | 2017-09-30 | 2017-10-31 | 2017-11-30 | 2017-12-31 | 2018-01-31 | 2018-02-28 | 2018-03-31
|  | Calculation based on connection limits | 60.98% | 60.86% | 60.47% | 60.94% | 60.76% | 65.68% | 99.78% | 100% | 99.82% | 99.68% | 100% | 99.32%
|  |  | 100% | 99.81% | 99.17% | 99.94% | 99.64% | 99.72% | 99.78% | 100% | 99.82% | 99.68% | 100% | 99.32%
|  |  | 0.60976 | 0.60858 | 0.60467 | 0.60936 | 0.60758 | 0.65684 | 0.99782 | 1 | 0.99817 | 0.99681 | 1 | 0.99316
|  |  | 1 | 0.99807 | 0.99167 | 0.99935 | 0.99643 | 0.99722 | 0.99782 | 1 | 0.99817 | 0.99681 | 1 | 0.99316
Month | Including Cable fault | Excluding Cable Fault
2017-04-30 | 60.98% | 100%
2017-05-31 | 60.86% | 99.81%
2017-06-30 | 60.47% | 99.17%
2017-07-31 | 60.94% | 99.94%
2017-08-31 | 60.76% | 99.64%
2017-09-30 | 65.68% | 99.72%
2017-10-31 | 99.78% | 99.78%
2017-11-30 | 100% | 100%
2017-12-31 | 99.82% | 99.82%
2018-01-31 | 99.68% | 99.68%
2018-02-28 | 100% | 100%
2018-03-31 | 99.32% | 99.32%

## Chart (hidden)
Enter period start date | 2014-04-01 | Date ok
Enter period duration | 12 | months
End date | 2015-04-01
Hours in period | 8760
Check | TRUE
Hours
Available | 10530.2333 | [10 empty] | Year from | 2004-04-01 | 2005-04-01 | 2006-04-01 | 2007-04-01 | 2008-04-01 | 2009-04-01 | 2010-04-01
Unavailable | -1770.2333 | [10 empty] | Year to | 2005-04-01 | 2006-04-01 | 2007-04-01 | 2008-04-01 | 2009-04-01 | 2010-04-01 | 2011-04-01
FO | -2533.9833
SO | 0
PO | 763.75
[14 empty] | 109.4 | 80.73 | 43.25 | 83.0997 | 572.2398 | 1803.209 |  |  | Apr | 410 | 410
| % | [20 empty] | May | 410 | 410
Available | 120.2% | [10 empty] | Fored outages/trips | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Jun | 410 | 378
Unavailable | -20.21% | [10 empty] | Scheduled/planned outages (excluding SP line outages) | 0 | 0 | -33.5 | 0 | -49.493 | -274 | #REF! |  |  | Jul | 410 | 250
Forced outage | -28.93% | [10 empty] | Scottish power line outages |  |  | 33.5 |  | 49.493 | 274 | #REF! |  |  | Aug | 410 | 250
Scheduled outage | 0% | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | #REF! |  |  | Sep | 410 | 250
Planned outage | 8.719% | [20 empty] | Oct | 410 | 250
[12 empty] | Availability | 8760 | 8760 | 8760 | 8784 | 8760 | 8760 | #REF! |  |  | Nov | 450 | 250
[12 empty] | Hours in year | 8760 | 8760 | 8760 | 8784 | 8760 | 8760 | 8760 |  |  | Dec | 450 | 250
[22 empty] | Jan | 450 | 250
[12 empty] | Availability | 100% | 100% | 100% | 100% | 100% | 100% | #REF! |  |  | Feb | 450 | 250
[12 empty] | Availability excluding SP outages | 100% | 100% | 100.4% | 100% | 100.6% | 103.1% | #REF! |  |  | Mar | 450 | 250
[23 empty] | 5120 | 3448 | 0.67344
[6 empty] | FO | SO | PO | Start date and end date cover entire outage | Start date after outage end date or end date before outage start | Start date after outage start date and end date before outage end date | Start date before outage start date but end date before outage end date | Start date after outage start date and end date after outage end date |  |  | Outage duration for period
2004-04-01 | 2004-04-01 01:07 | 400 | 1.12 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-04-05 | 2004-04-05 00:37 | 250 | 0.31 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-04-06 | 2004-04-06 00:23 | 400 | 0.38 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-10 | 2004-07-10 09:25 | 400 | 9.41 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-11 | 2004-07-12 | 400 | 24 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-12 | 2004-07-13 | 400 | 24 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-13 | 2004-07-14 | 400 | 24 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-14 | 2004-07-14 09:25 | 400 | 9.41 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-16 | 2004-07-16 02:35 | 250 | 1.29 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-09-03 | 2004-09-03 00:24 | 250 | 0.2 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-09-03 | 2004-09-03 00:40 | 250 | 0.33 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-10-01 | 2004-10-01 00:53 | 250 | 0.44 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-10-03 | 2004-10-03 06:37 | 250 | 3.31 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-10-29 | 2004-10-29 00:16 | 250 | 0.13 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-11-10 | 2004-11-10 00:32 | 250 | 0.27 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-11-14 | 2004-11-14 08:55 | 250 | 4.46 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-11-14 | 2004-11-14 00:23 | 250 | 0.19 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-05 | 2005-05-05 01:26 | 250 | 0.72 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-10 | 2005-05-10 08:30 | 250 | 4.25 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-11 | 2005-05-11 04:24 | 250 | 2.2 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-13 | 2005-05-13 00:07 | 250 | 0.06 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-23 | 2005-05-23 19:30 | 250 | 9.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-24 | 2005-05-25 | 250 | 12 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-25 | 2005-05-25 19:30 | 250 | 9.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-13 | 2005-06-13 15:15 | 250 | 7.625 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-14 | 2005-06-15 | 250 | 12 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-15 | 2005-06-15 15:15 | 250 | 7.625 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-19 | 2005-06-19 12:00 | 250 | 6 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-20 | 2005-06-20 02:18 | 250 | 1.15 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-20 | 2005-06-20 00:10 | 250 | 0.08 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-21 | 2005-06-21 00:20 | 400 | 0.34 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-07-12 | 2005-07-12 23:33 | 250 | 11.775 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-07-12 | 2005-07-12 03:12 | 250 | 1.6 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-07-13 | 2005-07-13 23:33 | 250 | 11.775 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-07-18 | 2005-07-18 09:00 | 250 | 4.5 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-08-03 | 2005-08-03 02:00 | 250 | 1 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-08-03 | 2005-08-03 04:30 | 250 | 2.25 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-09-13 | 2005-09-13 01:53 | 250 | 0.94 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-09-13 | 2005-09-13 00:12 | 250 | 0.1 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-10-13 | 2005-10-13 01:42 | 250 | 0.85 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-10-26 | 2005-10-26 02:07 | 250 | 1.06 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-04-02 | 2006-04-02 16:45 | 400 | 16.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-04-03 | 2006-04-03 16:45 | 400 | 16.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-06-27 | 2006-06-27 00:46 | 250 | 0.38 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-06-29 | 2006-06-29 04:44 | 250 | 2.37 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-06-29 | 2006-06-29 01:00 | 250 | 0.5 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-07-12 | 2006-07-12 19:04 | 250 | 9.53 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-07-13 | 2006-07-13 19:04 | 250 | 9.53 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-07-13 | 2006-07-13 02:10 | 250 | 1.08 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-07-25 | 2006-07-25 01:12 | 250 | 0.6 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-08-16 | 2006-08-16 01:30 | 250 | 0.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-08-16 | 2006-08-16 00:48 | 250 | 0.4 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-08-16 | 2006-08-16 05:31 | 250 | 2.76 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-08-25 | 2006-08-25 01:55 | 250 | 0.96 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-12-04 | 2006-12-04 00:58 | 250 | 0.48 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-12-13 | 2006-12-13 06:00 | 250 | 3 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-12-14 | 2006-12-14 19:36 | 250 | 9.8 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-01-18 | 2007-01-18 01:36 | 400 | 1.6 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-01-19 | 2007-01-19 01:36 | 400 | 1.6 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-02-05 | 2007-02-05 02:11 | 250 | 1.09 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-02-05 | 2007-02-05 01:36 | 250 | 0.8 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-04-04 | 2007-04-04 00:44 | 250 | 0.37 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-04-24 | 2007-04-24 02:30 | 250 | 1.25 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-12 | 2007-07-12 20:30 | 250 | 10.25 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-13 | 2007-07-13 20:30 | 250 | 10.25 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-13 | 2007-07-13 03:22 | 250 | 1.75 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-14 | 2007-07-14 18:31 | 250 | 9.63 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-15 | 2007-07-15 04:52 | 250 | 2.43 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-15 | 2007-07-15 01:19 | 250 | 0.66 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-11-28 | 2007-11-28 02:11 | 250 | 1.09 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-02-07 | 2008-02-07 01:00 | 250 | 0.5 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-02-07 | 2008-02-07 07:05 | 250 | 3.54 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-02-08 | 2008-02-08 01:00 | 250 | 0.5 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-03-02 | 2008-03-02 01:26 | 250 | 0.72 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-03-02 | 2008-03-02 00:37 | 250 | 0.31 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-05-12 23:52 | 2008-05-13 04:26 | 250 | 2.28 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-06-11 14:20 | 2008-06-11 14:40 | 250 | 0.165 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-06-23 19:36 | 2008-06-23 22:32 | 250 | 1.465 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-06-23 11:43 | 2008-06-23 13:23 | 250 | 0.835 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-05 15:14 | 2008-08-05 17:14 | 500 | 1.993 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-23 06:00 | 2008-08-24 06:00 | 500 | 24 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-23 04:30 | 2008-08-24 04:00 | 500 | 23.5 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-24 04:30 | 2008-08-25 04:30 | 250 | 12 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-24 06:00 | 2008-08-25 11:30 | 250 | 14.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-09-02 06:00 | 2008-09-02 06:30 | 250 | 0.25 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-11-22 | 2008-11-22 01:50 | 250 | 0.92 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-01-13 09:01 | 2009-01-13 10:54 | 250 | 0.94167 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-06-01 00:02 | 2009-06-01 10:26 | 250 | 5.2 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-06-08 12:52 | 2009-06-08 13:59 | 500 | 1.1167 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-07-02 06:30 | 2009-07-02 20:40 | 250 | 7.0833 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-07-13 18:25 | 2009-07-13 21:12 | 250 | 1.3875 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-09-28 08:00 | 2009-10-09 18:00 | 500 | 274 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-10-12 17:38 | 2009-10-12 20:07 | 250 | 1.24 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-10-16 17:38 | 2009-10-16 18:13 | 250 | 0.29 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-12-01 17:55 | 2009-12-01 20:40 | 250 | 1.373 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-12-21 15:36 | 2009-12-21 17:36 | 250 | 1.0043 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-01-06 16:04 | 2010-01-06 16:39 | 250 | 0.29167 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-01-21 18:37 | 2010-01-22 02:41 | 250 | 4.0333 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-02-16 13:03 | 2010-02-16 13:44 | 250 | 0.34 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-30 19:29 | 2010-03-30 21:27 | 250 | 0.98 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-30 19:29 | 2010-03-30 20:37 | 500 | 1.13 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-31 00:45 | 2010-03-31 01:10 | 250 | 0.21 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-31 01:34 | 2010-03-31 02:17 | 250 | 0.36 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-31 08:29 | 2010-03-31 08:39 | 250 | 0.08 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-31 08:44 | 2010-03-31 08:58 | 250 | 0.12 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-06-14 | 2010-07-08 | 500 | 576 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-09-09 12:41 | 2010-11-01 | 250 | 491.4407 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-11-01 | 2010-11-18 | 250 | 181.3333 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-11-01 | 2010-11-18 | 250 | 181.3333 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-11-01 | 2011-11-01 03:10 | 250 | 1.585 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-03-19 08:30 | 2011-03-19 10:12 | 250 | 0.85 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-05-25 15:47 | 2011-05-25 16:48 | 500 | 0.5 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-08-23 | 2011-08-26 | 250 | 36 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-06-26 04:17 | 2011-08-24 14:00 | 250 | 556.3772 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-08-24 14:00 | 2011-11-01 06:00 | 500 | 1648 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-11-01 06:00 | 2012-01-18 21:00 | 500 | 1887 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-01-18 21:00 | 2012-02-19 06:00 | 250 | 376.5 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-06-23 10:17 | 2012-11-01 | 250 | 1222.9137 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-11-01 | 2013-03-31 | 250 | 1600 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 2013-03-31 | 2012-11-01 | 150
2012-08-11 10:22 | 2012-08-11 11:25 | 250 | 0.63872 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-09-03 12:03 | 2012-09-04 00:17 | 250 | 4.774 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-10-01 08:58 | 2012-10-01 09:46 | 250 | 0.39024 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-11-27 06:00 | 2012-11-29 06:00 | 250 | 21.3333 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-01-18 16:38 | 2013-01-18 20:36 | 250 | 1.7616 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-03-22 00:59 | 2013-03-22 05:07 | 250 | 1.8356 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-03-22 10:49 | 2013-03-22 15:35 | 250 | 2.1156 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-03-22 18:24 | 2013-03-22 19:13 | 250 | 0.36889 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-03-22 19:31 | 2013-03-22 21:10 | 250 | 0.73333 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-04-23 21:08 | 2013-04-24 00:09 | 250 | 1.8401 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-04-01 | 2013-04-30 23:59 | 250 | 280.9691 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-05-01 | 2013-08-31 23:59 | 250 | 1151.9935 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-08-12 08:00 | 2013-09-20 06:00 | 250 | 569.5122 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-09-01 | 2013-11-01 06:00 | 250 | 573.6585 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-11-01 06:00 | 2014-03-31 06:00 | 250 | 1600 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2014-03-31 06:00 | 2014-05-01 06:00 | 250 | 290.3415 | 2005-04-01 | FO | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 363 |  |  | 363
2014-05-01 06:00 | 2013-08-31 23:59 | 250 | -2268.8846 | 2005-04-01 | FO | -2907.0083 | 0 | 0 | -2907.0083 | 0 | 0 | 0 | 0 |  |  | -2907.0083
2014-05-12 22:00 | 2014-05-13 07:00 | 250 | 5.4878 | 2005-04-01 | FO | 4.5 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 |  |  | 4.5
2014-05-14 05:53 | 2014-05-14 08:22 | 250 | 1.5142 | 2005-04-01 | FO | 1.2417 | 0 | 0 | 1.2417 | 0 | 0 | 0 | 0 |  |  | 1.2417
2014-05-18 06:00 | 2014-05-18 14:00 | 250 | 4.878 | 2005-04-01 | PO | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 |  |  | 4
2014-03-31 07:30 | 2014-04-07 15:30 | 250 | 107.3171 | 2005-04-01 | PO | 0 | 0 | 79.75 | 0 | 0 | 0 | 0 | 79.75 |  |  | 79.75
2014-06-29 05:24 | 2014-06-29 13:58 | 250 | 5.2236 | 2005-04-01 | FO | 4.2833 | 0 | 0 | 4.2833 | 0 | 0 | 0 | 0 |  |  | 4.2833
2014-07-05 08:30 | 2014-08-29 16:30 | 250 | 809.7561 | 2005-04-01 | PO | 0 | 0 | 664 | 664 | 0 | 0 | 0 | 0 |  |  | 664
2014-11-03 08:30 | 2014-11-04 16:30 | 250 | 19.5122 | 2005-04-01 | PO | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 |  |  | 16

## Chart 2 (hidden)
Enter period start date | 2011-03-01 | Date ok
Enter period duration | 12 | months
End date | 2012-03-01
[21 empty] | 410 | 225
[21 empty] | 410 | 225
Hours in period | 8784 | [19 empty] | 410 | 225
Check | TRUE | [19 empty] | 410 | 225
[21 empty] | 410 | 225
| Hours | [19 empty] | 410 | 225
Available | 6815.2565 | [10 empty] | Year from | 2004-04-01 | 2005-04-01 | 2006-04-01 | 2007-04-01 | 2008-04-01 | 2009-04-01 | 2010-04-01 |  | 410 | 225
Unavailable | 1968.7435 | [10 empty] | Year to | 2005-04-01 | 2006-04-01 | 2007-04-01 | 2008-04-01 | 2009-04-01 | 2010-04-01 | 2011-04-01 |  | 450 | 225
FO | 753.0795 | [11 empty] | 1 April 2005 | 1 April 2006 | 1 April 2007 | 1 April 2008 | 1 April 2009 | 1 April 2010 | 1 April 2011 |  | 450 | 225
SO | 603.664 | [19 empty] | 450 | 225
PO | 612 | [19 empty] | 450 | 225
[14 empty] | 109.4 | 80.73 | 43.25 | 83.0997 | 572.2398 | 1803.209 |  | 450 | 225
%
Available | 77.59% | [10 empty] | Fored outages/trips | 4 | 24.82 | 9.38 | 15.95 | 0.92 | 25.2355 | 672.774 |  | 5120 | 2700 | 0.52734
Unavailable | 22.41% | [10 empty] | Scheduled/planned outages (excluding SP line outages) | 99.25 | 84.58 | 37.85 | 27.3 | 32.6867 | 1.0043 | #REF! |  |  |  | 0.47266
Forced outage | 8.573% | [10 empty] | Scottish power line outages |  |  | 33.5 |  | 49.493 | 274 | #REF!
Scheduled outage | 6.872% | [11 empty] | 103.25 | 109.4 | 80.73 | 43.25 | 83.0997 | 300.2398 | #REF!
Planned outage | 6.967%
[12 empty] | Availability | 8656.75 | 8650.6 | 8679.27 | 8740.75 | 8676.9003 | 8459.7602 | #REF!
[12 empty] | Hours in year | 8760 | 8760 | 8760 | 8784 | 8760 | 8760 | 8760 | Feb | 450 | 318.9655 | 70.88%
[20 empty] | Mar | 450 | 450 | 100%
[12 empty] | Availability | 98.82% | 98.75% | 99.08% | 99.51% | 99.05% | 96.57% | #REF! | Apr | 410 | 410 | 100%
[12 empty] | Availability excluding Scottish Power line outages | 98.82% | 98.75% | 99.46% | 99.51% | 99.62% | 99.7% | #REF! | May | 410 | 410 | 100%
[20 empty] | Jun | 410 | 410 | 100%
[20 empty] | Jul | 410 | 250 | 60.98%
[20 empty] | Aug | 410 | 250 | 60.98%
[20 empty] | Sep | 410 | 250 | 60.98%
[20 empty] | Oct | 410 | 250 | 60.98%
[20 empty] | Nov | 450 | 250 | 55.56%
[20 empty] | Dec | 450 | 250 | 55.56%
[20 empty] | Jan | 450 | 250 | 55.56%
`
[6 empty] | FO | SO | PO | Start date and end date cover entire outage | Start date after outage end date or end date before outage start | Start date after outage start date and end date before outage end date | Start date before outage start date but end date before outage end date | Start date after outage start date and end date after outage end date |  |  | Outage duration for period
2004-04-01 | 2004-04-01 01:07 | 500 | 1.12 | 2005-04-01 | FO | 1.12 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 |  |  | 1.12
2004-04-05 | 2004-04-05 00:37 | 250 | 0.31 | 2005-04-01 | FO | 0.31 | 0 | 0 | 0.31 | 0 | 0 | 0 | 0 |  |  | 0.31
2004-04-06 | 2004-04-06 00:23 | 500 | 0.38 | 2005-04-01 | FO | 0.38 | 0 | 0 | 0.38 | 0 | 0 | 0 | 0 |  |  | 0.38
2004-07-10 | 2004-07-10 09:25 | 500 | 9.41 | 2005-04-01 | SO | 0 | 9.41 | 0 | 9.41 | 0 | 0 | 0 | 0 |  |  | 9.41
2004-07-11 | 2004-07-12 | 500 | 24 | 2005-04-01 | SO | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 0 |  |  | 24
2004-07-12 | 2004-07-13 | 500 | 24 | 2005-04-01 | SO | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 0 |  |  | 24
2004-07-13 | 2004-07-14 | 500 | 24 | 2005-04-01 | SO | 0 | 24 | 0 | 24 | 0 | 0 | 0 | 0 |  |  | 24
2004-07-14 | 2004-07-14 09:25 | 500 | 9.41 | 2005-04-01 | SO | 0 | 9.41 | 0 | 9.41 | 0 | 0 | 0 | 0 |  |  | 9.41
2004-07-16 | 2004-07-16 02:35 | 250 | 1.29 | 2005-04-01 | FO | 1.29 | 0 | 0 | 1.29 | 0 | 0 | 0 | 0 |  |  | 1.29
2004-09-03 | 2004-09-03 00:24 | 250 | 0.2 | 2005-04-01 | SO | 0 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 0 |  |  | 0.2
2004-09-03 | 2004-09-03 00:40 | 250 | 0.33 | 2005-04-01 | SO | 0 | 0.33 | 0 | 0.33 | 0 | 0 | 0 | 0 |  |  | 0.33
2004-10-01 | 2004-10-01 00:53 | 250 | 0.44 | 2005-04-01 | FO | 0.44 | 0 | 0 | 0.44 | 0 | 0 | 0 | 0 |  |  | 0.44
2004-10-03 | 2004-10-03 06:37 | 250 | 3.31 | 2005-04-01 | SO | 0 | 3.31 | 0 | 3.31 | 0 | 0 | 0 | 0 |  |  | 3.31
2004-10-29 | 2004-10-29 00:16 | 250 | 0.13 | 2005-04-01 | SO | 0 | 0.13 | 0 | 0.13 | 0 | 0 | 0 | 0 |  |  | 0.13
2004-11-10 | 2004-11-10 00:32 | 250 | 0.27 | 2005-04-01 | FO | 0.27 | 0 | 0 | 0.27 | 0 | 0 | 0 | 0 |  |  | 0.27
2004-11-14 | 2004-11-14 08:55 | 250 | 4.46 | 2005-04-01 | SO | 0 | 4.46 | 0 | 4.46 | 0 | 0 | 0 | 0 |  |  | 4.46
2004-11-14 | 2004-11-14 00:23 | 250 | 0.19 | 2005-04-01 | FO | 0.19 | 0 | 0 | 0.19 | 0 | 0 | 0 | 0 |  |  | 0.19
2005-05-05 | 2005-05-05 01:26 | 250 | 0.72 | 2006-04-01 | FO | 0.72 | 0 | 0 | 0.72 | 0 | 0 | 0 | 0 |  |  | 0.72
2005-05-10 | 2005-05-10 08:30 | 250 | 4.25 | 2006-04-01 | FO | 4.25 | 0 | 0 | 4.25 | 0 | 0 | 0 | 0 |  |  | 4.25
2005-05-11 | 2005-05-11 04:24 | 250 | 2.2 | 2006-04-01 | FO | 2.2 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 |  |  | 2.2
2005-05-13 | 2005-05-13 00:07 | 250 | 0.06 | 2006-04-01 | FO | 0.06 | 0 | 0 | 0.06 | 0 | 0 | 0 | 0 |  |  | 0.06
2005-05-23 | 2005-05-23 19:30 | 250 | 9.75 | 2006-04-01 | SO | 0 | 9.75 | 0 | 9.75 | 0 | 0 | 0 | 0 |  |  | 9.75
2005-05-24 | 2005-05-25 | 250 | 12 | 2006-04-01 | SO | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 0 |  |  | 12
2005-05-25 | 2005-05-25 19:30 | 250 | 9.75 | 2006-04-01 | SO | 0 | 9.75 | 0 | 9.75 | 0 | 0 | 0 | 0 |  |  | 9.75
2005-06-13 | 2005-06-13 15:15 | 250 | 7.625 | 2006-04-01 | SO | 0 | 7.625 | 0 | 7.625 | 0 | 0 | 0 | 0 |  |  | 7.625
2005-06-14 | 2005-06-15 | 250 | 12 | 2006-04-01 | SO | 0 | 12 | 0 | 12 | 0 | 0 | 0 | 0 |  |  | 12
2005-06-15 | 2005-06-15 15:15 | 250 | 7.625 | 2006-04-01 | SO | 0 | 7.625 | 0 | 7.625 | 0 | 0 | 0 | 0 |  |  | 7.625
2005-06-19 | 2005-06-19 12:00 | 250 | 6 | 2006-04-01 | FO | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 |  |  | 6
2005-06-20 | 2005-06-20 02:18 | 250 | 1.15 | 2006-04-01 | FO | 1.15 | 0 | 0 | 1.15 | 0 | 0 | 0 | 0 |  |  | 1.15
2005-06-20 | 2005-06-20 00:10 | 250 | 0.08 | 2006-04-01 | FO | 0.08 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 |  |  | 0.08
2005-06-21 | 2005-06-21 00:20 | 500 | 0.34 | 2006-04-01 | SO | 0 | 0.34 | 0 | 0.34 | 0 | 0 | 0 | 0 |  |  | 0.34
2005-07-12 | 2005-07-12 23:33 | 250 | 11.775 | 2006-04-01 | SO | 0 | 11.775 | 0 | 11.775 | 0 | 0 | 0 | 0 |  |  | 11.775
2005-07-12 | 2005-07-12 03:12 | 250 | 1.6 | 2006-04-01 | FO | 1.6 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 |  |  | 1.6
2005-07-13 | 2005-07-13 23:33 | 250 | 11.775 | 2006-04-01 | SO | 0 | 11.775 | 0 | 11.775 | 0 | 0 | 0 | 0 |  |  | 11.775
2005-07-18 | 2005-07-18 09:00 | 250 | 4.5 | 2006-04-01 | FO | 4.5 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 |  |  | 4.5
2005-08-03 | 2005-08-03 02:00 | 250 | 1 | 2006-04-01 | SO | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 1
2005-08-03 | 2005-08-03 04:30 | 250 | 2.25 | 2006-04-01 | FO | 2.25 | 0 | 0 | 2.25 | 0 | 0 | 0 | 0 |  |  | 2.25
2005-09-13 | 2005-09-13 01:53 | 250 | 0.94 | 2006-04-01 | SO | 0 | 0.94 | 0 | 0.94 | 0 | 0 | 0 | 0 |  |  | 0.94
2005-09-13 | 2005-09-13 00:12 | 250 | 0.1 | 2006-04-01 | FO | 0.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | 0.1
2005-10-13 | 2005-10-13 01:42 | 250 | 0.85 | 2006-04-01 | FO | 0.85 | 0 | 0 | 0.85 | 0 | 0 | 0 | 0 |  |  | 0.85
2005-10-26 | 2005-10-26 02:07 | 250 | 1.06 | 2006-04-01 | FO | 1.06 | 0 | 0 | 1.06 | 0 | 0 | 0 | 0 |  |  | 1.06
2006-04-02 | 2006-04-02 16:45 | 500 | 16.75 | 2007-04-01 | SO | 0 | 16.75 | 0 | 16.75 | 0 | 0 | 0 | 0 |  |  | 16.75
2006-04-03 | 2006-04-03 16:45 | 500 | 16.75 | 2007-04-01 | SO | 0 | 16.75 | 0 | 16.75 | 0 | 0 | 0 | 0 |  |  | 16.75
2006-06-27 | 2006-06-27 00:46 | 250 | 0.38 | 2007-04-01 | FO | 0.38 | 0 | 0 | 0.38 | 0 | 0 | 0 | 0 |  |  | 0.38
2006-06-29 | 2006-06-29 04:44 | 250 | 2.37 | 2007-04-01 | FO | 2.37 | 0 | 0 | 2.37 | 0 | 0 | 0 | 0 |  |  | 2.37
2006-06-29 | 2006-06-29 01:00 | 250 | 0.5 | 2007-04-01 | FO | 0.5 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 |  |  | 0.5
2006-07-12 | 2006-07-12 19:04 | 250 | 9.53 | 2007-04-01 | SO | 0 | 9.53 | 0 | 9.53 | 0 | 0 | 0 | 0 |  |  | 9.53
2006-07-13 | 2006-07-13 19:04 | 250 | 9.53 | 2007-04-01 | SO | 0 | 9.53 | 0 | 9.53 | 0 | 0 | 0 | 0 |  |  | 9.53
2006-07-13 | 2006-07-13 02:10 | 250 | 1.08 | 2007-04-01 | FO | 1.08 | 0 | 0 | 1.08 | 0 | 0 | 0 | 0 |  |  | 1.08
2006-07-25 | 2006-07-25 01:12 | 250 | 0.6 | 2007-04-01 | SO | 0 | 0.6 | 0 | 0.6 | 0 | 0 | 0 | 0 |  |  | 0.6
2006-08-16 | 2006-08-16 01:30 | 250 | 0.75 | 2007-04-01 | SO | 0 | 0.75 | 0 | 0.75 | 0 | 0 | 0 | 0 |  |  | 0.75
2006-08-16 | 2006-08-16 00:48 | 250 | 0.4 | 2007-04-01 | FO | 0.4 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 |  |  | 0.4
2006-08-16 | 2006-08-16 05:31 | 250 | 2.76 | 2007-04-01 | FO | 2.76 | 0 | 0 | 2.76 | 0 | 0 | 0 | 0 |  |  | 2.76
2006-08-25 | 2006-08-25 01:55 | 250 | 0.96 | 2007-04-01 | SO | 0 | 0.96 | 0 | 0.96 | 0 | 0 | 0 | 0 |  |  | 0.96
2006-12-04 | 2006-12-04 00:58 | 250 | 0.48 | 2007-04-01 | SO | 0 | 0.48 | 0 | 0.48 | 0 | 0 | 0 | 0 |  |  | 0.48
2006-12-13 | 2006-12-13 06:00 | 250 | 3 | 2007-04-01 | SO | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 |  |  | 3
2006-12-14 | 2006-12-14 19:36 | 250 | 9.8 | 2007-04-01 | SO | 0 | 9.8 | 0 | 9.8 | 0 | 0 | 0 | 0 |  |  | 9.8
2007-01-18 | 2007-01-18 01:36 | 500 | 1.6 | 2007-04-01 | SO | 0 | 1.6 | 0 | 1.6 | 0 | 0 | 0 | 0 |  |  | 1.6
2007-01-19 | 2007-01-19 01:36 | 500 | 1.6 | 2007-04-01 | SO | 0 | 1.6 | 0 | 1.6 | 0 | 0 | 0 | 0 |  |  | 1.6
2007-02-05 | 2007-02-05 02:11 | 250 | 1.09 | 2007-04-01 | FO | 1.09 | 0 | 0 | 1.09 | 0 | 0 | 0 | 0 |  |  | 1.09
2007-02-05 | 2007-02-05 01:36 | 250 | 0.8 | 2007-04-01 | FO | 0.8 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 |  |  | 0.8
2007-04-04 | 2007-04-04 00:44 | 250 | 0.37 | 2008-04-01 | SO | 0 | 0.37 | 0 | 0.37 | 0 | 0 | 0 | 0 |  |  | 0.37
2007-04-24 | 2007-04-24 02:30 | 250 | 1.25 | 2008-04-01 | SO | 0 | 1.25 | 0 | 1.25 | 0 | 0 | 0 | 0 |  |  | 1.25
2007-07-12 | 2007-07-12 20:30 | 250 | 10.25 | 2008-04-01 | SO | 0 | 10.25 | 0 | 10.25 | 0 | 0 | 0 | 0 |  |  | 10.25
2007-07-13 | 2007-07-13 20:30 | 250 | 10.25 | 2008-04-01 | SO | 0 | 10.25 | 0 | 10.25 | 0 | 0 | 0 | 0 |  |  | 10.25
2007-07-13 | 2007-07-13 03:22 | 260 | 1.75 | 2008-04-01 | FO | 1.75 | 0 | 0 | 1.75 | 0 | 0 | 0 | 0 |  |  | 1.75
2007-07-14 | 2007-07-14 18:31 | 260 | 9.63 | 2008-04-01 | FO | 9.63 | 0 | 0 | 9.63 | 0 | 0 | 0 | 0 |  |  | 9.63
2007-07-15 | 2007-07-15 04:52 | 250 | 2.43 | 2008-04-01 | SO | 0 | 2.43 | 0 | 2.43 | 0 | 0 | 0 | 0 |  |  | 2.43
2007-07-15 | 2007-07-15 01:19 | 250 | 0.66 | 2008-04-01 | SO | 0 | 0.66 | 0 | 0.66 | 0 | 0 | 0 | 0 |  |  | 0.66
2007-11-28 | 2007-11-28 02:11 | 250 | 1.09 | 2008-04-01 | SO | 0 | 1.09 | 0 | 1.09 | 0 | 0 | 0 | 0 |  |  | 1.09
2008-02-07 | 2008-02-07 01:00 | 250 | 0.5 | 2008-04-01 | SO | 0 | 0.5 | 0 | 0.5 | 0 | 0 | 0 | 0 |  |  | 0.5
2008-02-07 | 2008-02-07 07:05 | 250 | 3.54 | 2008-04-01 | FO | 3.54 | 0 | 0 | 3.54 | 0 | 0 | 0 | 0 |  |  | 3.54
2008-02-08 | 2008-02-08 01:00 | 250 | 0.5 | 2008-04-01 | SO | 0 | 0.5 | 0 | 0.5 | 0 | 0 | 0 | 0 |  |  | 0.5
2008-03-02 | 2008-03-02 01:26 | 250 | 0.72 | 2008-04-01 | FO | 0.72 | 0 | 0 | 0.72 | 0 | 0 | 0 | 0 |  |  | 0.72
2008-03-02 | 2008-03-02 00:37 | 250 | 0.31 | 2008-04-01 | FO | 0.31 | 0 | 0 | 0.31 | 0 | 0 | 0 | 0 |  |  | 0.31
2008-05-12 23:52 | 2008-05-13 04:26 | 250 | 2.28 | 2009-04-01 | SO | 0 | 2.28 | 0 | 2.28 | 0 | 0 | 0 | 0 |  |  | 2.28
2008-06-11 14:20 | 2008-06-11 14:40 | 250 | 0.165 | 2009-04-01 | SO | 0 | 0.165 | 0 | 0.165 | 0 | 0 | 0 | 0 |  |  | 0.165
2008-06-23 19:36 | 2008-06-23 22:32 | 250 | 1.465 | 2009-04-01 | SO | 0 | 1.465 | 0 | 1.465 | 0 | 0 | 0 | 0 |  |  | 1.465
2008-06-23 11:43 | 2008-06-23 13:23 | 250 | 0.835 | 2009-04-01 | SO | 0 | 0.835 | 0 | 0.835 | 0 | 0 | 0 | 0 |  |  | 0.835
2008-08-05 15:14 | 2008-08-05 17:14 | 500 | 1.993 | 2009-04-01 | SO | 0 | 1.993 | 0 | 1.993 | 0 | 0 | 0 | 0 |  |  | 1.993
2008-08-23 06:00 | 2008-08-24 06:00 | 500 | 24 | 2009-04-01 | PO | 0 | 0 | 24 | 24 | 0 | 0 | 0 | 0 |  |  | 24
2008-08-23 04:30 | 2008-08-24 04:00 | 500 | 23.5 | 2009-04-01 | SO | 0 | 23.5 | 0 | 23.5 | 0 | 0 | 0 | 0 |  |  | 23.5
2008-08-24 04:30 | 2008-08-25 04:30 | 250 | 12 | 2009-04-01 | PO | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 |  |  | 12
2008-08-24 06:00 | 2008-08-25 11:30 | 250 | 14.75 | 2009-04-01 | SO | 0 | 14.75 | 0 | 14.75 | 0 | 0 | 0 | 0 |  |  | 14.75
2008-09-02 06:00 | 2008-09-02 06:30 | 250 | 0.25 | 2009-04-01 | SO | 0 | 0.25 | 0 | 0.25 | 0 | 0 | 0 | 0 |  |  | 0.25
2008-11-22 | 2008-11-22 01:50 | 250 | 0.92 | 2009-04-01 | FO | 0.92 | 0 | 0 | 0.92 | 0 | 0 | 0 | 0 |  |  | 0.92
2009-01-13 09:01 | 2009-01-13 10:54 | 250 | 0.94167 | 2009-04-01 | SO | 0 | 0.94167 | 0 | 0.94167 | 0 | 0 | 0 | 0 |  |  | 0.94167
2009-06-01 00:02 | 2009-06-01 10:26 | 250 | 5.2 | 2010-04-01 | FO | 5.2 | 0 | 0 | 5.2 | 0 | 0 | 0 | 0 |  |  | 5.2
2009-06-08 12:52 | 2009-06-08 13:59 | 500 | 1.1167 | 2010-04-01 | FO | 1.1167 | 0 | 0 | 1.1167 | 0 | 0 | 0 | 0 |  |  | 1.1167
2009-07-02 06:30 | 2009-07-02 20:40 | 250 | 7.0833 | 2010-04-01 | FO | 7.0833 | 0 | 0 | 7.0833 | 0 | 0 | 0 | 0 |  |  | 7.0833
2009-07-13 18:25 | 2009-07-13 21:12 | 250 | 1.3875 | 2010-04-01 | FO | 1.3875 | 0 | 0 | 1.3875 | 0 | 0 | 0 | 0 |  |  | 1.3875
2009-09-28 08:00 | 2009-10-09 18:00 | 500 | 274 | 2010-04-01 | SO | 0 | 274 | 0 | 274 | 0 | 0 | 0 | 0 |  |  | 274
2009-10-12 17:38 | 2009-10-12 20:07 | 250 | 1.24 | 2010-04-01 | FO | 1.24 | 0 | 0 | 1.24 | 0 | 0 | 0 | 0 |  |  | 1.24
2009-10-16 17:38 | 2009-10-16 18:13 | 250 | 0.29 | 2010-04-01 | FO | 0.29 | 0 | 0 | 0.29 | 0 | 0 | 0 | 0 |  |  | 0.29
2009-12-01 17:55 | 2009-12-01 20:40 | 250 | 1.373 | 2010-04-01 | FO | 1.373 | 0 | 0 | 1.373 | 0 | 0 | 0 | 0 |  |  | 1.373
2009-12-21 15:36 | 2009-12-21 17:36 | 250 | 1.0043 | 2010-04-01 | SO | 0 | 1.0043 | 0 | 1.0043 | 0 | 0 | 0 | 0 |  |  | 1.0043
2010-01-06 16:04 | 2010-01-06 16:39 | 250 | 0.29167 | 2010-04-01 | FO | 0.29167 | 0 | 0 | 0.29167 | 0 | 0 | 0 | 0 |  |  | 0.29167
2010-01-21 18:37 | 2010-01-22 02:41 | 250 | 4.0333 | 2010-04-01 | FO | 4.0333 | 0 | 0 | 4.0333 | 0 | 0 | 0 | 0 |  |  | 4.0333
2010-02-16 13:03 | 2010-02-16 13:44 | 250 | 0.34 | 2010-04-01 | FO | 0.34 | 0 | 0 | 0.34 | 0 | 0 | 0 | 0 |  |  | 0.34
2010-03-30 19:29 | 2010-03-30 21:27 | 250 | 0.98 | 2010-04-01 | FO | 0.98 | 0 | 0 | 0.98 | 0 | 0 | 0 | 0 |  |  | 0.98
2010-03-30 19:29 | 2010-03-30 20:37 | 500 | 1.13 | 2010-04-01 | FO | 1.13 | 0 | 0 | 1.13 | 0 | 0 | 0 | 0 |  |  | 1.13
2010-03-31 00:45 | 2010-03-31 01:10 | 250 | 0.21 | 2010-04-01 | FO | 0.21 | 0 | 0 | 0.21 | 0 | 0 | 0 | 0 |  |  | 0.21
2010-03-31 01:34 | 2010-03-31 02:17 | 250 | 0.36 | 2010-04-01 | FO | 0.36 | 0 | 0 | 0.36 | 0 | 0 | 0 | 0 |  |  | 0.36
2010-03-31 08:29 | 2010-03-31 08:39 | 250 | 0.08 | 2010-04-01 | FO | 0.08 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 |  |  | 0.08
2010-03-31 08:44 | 2010-03-31 08:58 | 250 | 0.12 | 2010-04-01 | FO | 0.12 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 |  |  | 0.12
2010-06-14 | 2010-07-08 | 500 | 576 | 2011-04-01 | PO | 0 | 0 | 576 | 576 | 0 | 0 | 0 | 0 |  |  | 576
2010-09-09 12:41 | 2010-11-01 | 250 | 491.4407 | 2011-04-01 | FO | 491.4407 | 0 | 0 | 491.4407 | 0 | 0 | 0 | 0 |  |  | 491.4407
2010-11-01 | 2010-11-18 | 250 | 181.3333 | 2011-04-01 | FO | 181.3333 | 0 | 0 | 181.3333 | 0 | 0 | 0 | 0 |  |  | 181.3333
2011-11-01 | 2011-11-01 03:10 | 250 | 1.585 | 2011-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-08-23 | 2011-08-26 | 250 | 36 | 2011-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 | 2011-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 | 2012-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 | 2012-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0

## Chart (2) (hidden)
Enter period start date | 2014-04-01 | Date ok
Enter period duration | 12 | months
End date | 2015-04-01
Hours in period | 8760
Check | TRUE
Hours
Available | 9801.9394 | [10 empty] | Year from | 2004-04-01 | 2005-04-01 | 2006-04-01 | 2007-04-01 | 2008-04-01 | 2009-04-01 | 2010-04-01
Unavailable | -1041.9394 | [10 empty] | Year to | 2005-04-01 | 2006-04-01 | 2007-04-01 | 2008-04-01 | 2009-04-01 | 2010-04-01 | 2011-04-01
FO | -1973.3419
SO | 0
PO | 931.4024
[14 empty] | 109.4 | 80.73 | 43.25 | 83.0997 | 572.2398 | 1803.209 |  |  | Apr | 410 | 410
| % | [20 empty] | May | 410 | 410
Available | 111.9% | [10 empty] | Fored outages/trips | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Jun | 410 | 378
Unavailable | -11.89% | [10 empty] | Scheduled/planned outages (excluding SP line outages) | 0 | 0 | -33.5 | 0 | -49.493 | -274 | #REF! |  |  | Jul | 410 | 250
Forced outage | -22.53% | [10 empty] | Scottish power line outages |  |  | 33.5 |  | 49.493 | 274 | #REF! |  |  | Aug | 410 | 250
Scheduled outage | 0% | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | #REF! |  |  | Sep | 410 | 250
Planned outage | 10.63% | [20 empty] | Oct | 410 | 250
[12 empty] | Availability | 8760 | 8760 | 8760 | 8784 | 8760 | 8760 | #REF! |  |  | Nov | 450 | 250
[12 empty] | Hours in year | 8760 | 8760 | 8760 | 8784 | 8760 | 8760 | 8760 |  |  | Dec | 450 | 250
[22 empty] | Jan | 450 | 250
[12 empty] | Availability | 100% | 100% | 100% | 100% | 100% | 100% | #REF! |  |  | Feb | 450 | 250
[12 empty] | Availability excluding SP outages | 100% | 100% | 100.4% | 100% | 100.6% | 103.1% | #REF! |  |  | Mar | 450 | 250
[23 empty] | 5120 | 3448 | 0.67344
[6 empty] | FO | SO | PO | Start date and end date cover entire outage | Start date after outage end date or end date before outage start | Start date after outage start date and end date before outage end date | Start date before outage start date but end date before outage end date | Start date after outage start date and end date after outage end date |  |  | Outage duration for period
2004-04-01 | 2004-04-01 01:07 | 400 | 1.12 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-04-05 | 2004-04-05 00:37 | 150 | 0.31 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-04-06 | 2004-04-06 00:23 | 400 | 0.38 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-10 | 2004-07-10 09:25 | 400 | 9.41 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-11 | 2004-07-12 | 400 | 24 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-12 | 2004-07-13 | 400 | 24 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-13 | 2004-07-14 | 400 | 24 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-14 | 2004-07-14 09:25 | 400 | 9.41 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-07-16 | 2004-07-16 02:35 | 150 | 1.29 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-09-03 | 2004-09-03 00:24 | 150 | 0.2 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-09-03 | 2004-09-03 00:40 | 150 | 0.33 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-10-01 | 2004-10-01 00:53 | 150 | 0.44 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-10-03 | 2004-10-03 06:37 | 150 | 3.31 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-10-29 | 2004-10-29 00:16 | 150 | 0.13 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-11-10 | 2004-11-10 00:32 | 150 | 0.27 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-11-14 | 2004-11-14 08:55 | 150 | 4.46 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2004-11-14 | 2004-11-14 00:23 | 150 | 0.19 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-05 | 2005-05-05 01:26 | 150 | 0.72 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-10 | 2005-05-10 08:30 | 150 | 4.25 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-11 | 2005-05-11 04:24 | 150 | 2.2 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-13 | 2005-05-13 00:07 | 150 | 0.06 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-23 | 2005-05-23 19:30 | 150 | 9.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-24 | 2005-05-25 | 150 | 12 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-05-25 | 2005-05-25 19:30 | 150 | 9.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-13 | 2005-06-13 15:15 | 150 | 7.625 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-14 | 2005-06-15 | 150 | 12 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-15 | 2005-06-15 15:15 | 150 | 7.625 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-19 | 2005-06-19 12:00 | 150 | 6 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-20 | 2005-06-20 02:18 | 150 | 1.15 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-20 | 2005-06-20 00:10 | 150 | 0.08 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-06-21 | 2005-06-21 00:20 | 400 | 0.34 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-07-12 | 2005-07-12 23:33 | 150 | 11.775 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-07-12 | 2005-07-12 03:12 | 150 | 1.6 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-07-13 | 2005-07-13 23:33 | 150 | 11.775 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-07-18 | 2005-07-18 09:00 | 150 | 4.5 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-08-03 | 2005-08-03 02:00 | 150 | 1 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-08-03 | 2005-08-03 04:30 | 150 | 2.25 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-09-13 | 2005-09-13 01:53 | 150 | 0.94 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-09-13 | 2005-09-13 00:12 | 150 | 0.1 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-10-13 | 2005-10-13 01:42 | 150 | 0.85 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2005-10-26 | 2005-10-26 02:07 | 150 | 1.06 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-04-02 | 2006-04-02 16:45 | 400 | 16.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-04-03 | 2006-04-03 16:45 | 400 | 16.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-06-27 | 2006-06-27 00:46 | 150 | 0.38 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-06-29 | 2006-06-29 04:44 | 150 | 2.37 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-06-29 | 2006-06-29 01:00 | 150 | 0.5 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-07-12 | 2006-07-12 19:04 | 150 | 9.53 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-07-13 | 2006-07-13 19:04 | 150 | 9.53 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-07-13 | 2006-07-13 02:10 | 150 | 1.08 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-07-25 | 2006-07-25 01:12 | 150 | 0.6 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-08-16 | 2006-08-16 01:30 | 150 | 0.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-08-16 | 2006-08-16 00:48 | 150 | 0.4 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-08-16 | 2006-08-16 05:31 | 150 | 2.76 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-08-25 | 2006-08-25 01:55 | 150 | 0.96 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-12-04 | 2006-12-04 00:58 | 150 | 0.48 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-12-13 | 2006-12-13 06:00 | 150 | 3 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2006-12-14 | 2006-12-14 19:36 | 150 | 9.8 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-01-18 | 2007-01-18 01:36 | 400 | 1.6 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-01-19 | 2007-01-19 01:36 | 400 | 1.6 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-02-05 | 2007-02-05 02:11 | 150 | 1.09 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-02-05 | 2007-02-05 01:36 | 150 | 0.8 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-04-04 | 2007-04-04 00:44 | 150 | 0.37 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-04-24 | 2007-04-24 02:30 | 150 | 1.25 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-12 | 2007-07-12 20:30 | 150 | 10.25 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-13 | 2007-07-13 20:30 | 150 | 10.25 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-13 | 2007-07-13 03:22 | 160 | 1.75 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-14 | 2007-07-14 18:31 | 160 | 9.63 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-15 | 2007-07-15 04:52 | 150 | 2.43 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-07-15 | 2007-07-15 01:19 | 150 | 0.66 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2007-11-28 | 2007-11-28 02:11 | 200 | 1.09 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-02-07 | 2008-02-07 01:00 | 200 | 0.5 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-02-07 | 2008-02-07 07:05 | 200 | 3.54 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-02-08 | 2008-02-08 01:00 | 200 | 0.5 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-03-02 | 2008-03-02 01:26 | 200 | 0.72 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-03-02 | 2008-03-02 00:37 | 200 | 0.31 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-05-12 23:52 | 2008-05-13 04:26 | 160 | 2.28 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-06-11 14:20 | 2008-06-11 14:40 | 160 | 0.165 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-06-23 19:36 | 2008-06-23 22:32 | 160 | 1.465 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-06-23 11:43 | 2008-06-23 13:23 | 160 | 0.835 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-05 15:14 | 2008-08-05 17:14 | 410 | 1.993 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-23 06:00 | 2008-08-24 06:00 | 410 | 24 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-23 04:30 | 2008-08-24 04:00 | 410 | 23.5 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-24 04:30 | 2008-08-25 04:30 | 160 | 12 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-08-24 06:00 | 2008-08-25 11:30 | 160 | 14.75 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-09-02 06:00 | 2008-09-02 06:30 | 160 | 0.25 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2008-11-22 | 2008-11-22 01:50 | 160 | 0.92 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-01-13 09:01 | 2009-01-13 10:54 | 200 | 0.94167 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-06-01 00:02 | 2009-06-01 10:26 | 160 | 5.2 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-06-08 12:52 | 2009-06-08 13:59 | 410 | 1.1167 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-07-02 06:30 | 2009-07-02 20:40 | 160 | 7.0833 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-07-13 18:25 | 2009-07-13 21:12 | 160 | 1.3875 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-09-28 08:00 | 2009-10-09 18:00 | 410 | 274 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-10-12 17:38 | 2009-10-12 20:07 | 160 | 1.24 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-10-16 17:38 | 2009-10-16 18:13 | 160 | 0.29 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-12-01 17:55 | 2009-12-01 20:40 | 200 | 1.373 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2009-12-21 15:36 | 2009-12-21 17:36 | 200 | 1.0043 | 2005-04-01 | SO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-01-06 16:04 | 2010-01-06 16:39 | 200 | 0.29167 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-01-21 18:37 | 2010-01-22 02:41 | 200 | 4.0333 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-02-16 13:03 | 2010-02-16 13:44 | 200 | 0.34 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-30 19:29 | 2010-03-30 21:27 | 200 | 0.98 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-30 19:29 | 2010-03-30 20:37 | 450 | 1.13 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-31 00:45 | 2010-03-31 01:10 | 200 | 0.21 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-31 01:34 | 2010-03-31 02:17 | 200 | 0.36 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-31 08:29 | 2010-03-31 08:39 | 200 | 0.08 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-03-31 08:44 | 2010-03-31 08:58 | 200 | 0.12 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-06-14 | 2010-07-08 | 410 | 576 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-09-09 12:41 | 2010-11-01 | 160 | 491.4407 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2010-11-01 | 2010-11-18 | 200 | 181.3333 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-11-01 | 2011-11-01 03:10 | 200 | 1.585 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-03-19 08:30 | 2011-03-19 10:12 | 200 | 0.85 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-05-25 15:47 | 2011-05-25 16:48 | 410 | 0.5 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-08-23 | 2011-08-26 | 160 | 36 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-06-26 04:17 | 2011-08-24 14:00 | 160 | 556.3772 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-08-24 14:00 | 2011-11-01 06:00 | 410 | 1648 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2011-11-01 06:00 | 2012-01-18 21:00 | 450 | 1887 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-01-18 21:00 | 2012-02-19 06:00 | 225 | 376.5 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-06-23 10:17 | 2012-11-01 | 160 | 1222.9137 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-11-01 | 2013-03-31 | 200 | 1600 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-08-11 10:22 | 2012-08-11 11:25 | 250 | 0.63872 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 2013-03-31 | 2012-11-01 | 150
2012-09-03 12:03 | 2012-09-04 00:17 | 160 | 4.774 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-10-01 08:58 | 2012-10-01 09:46 | 160 | 0.39024 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2012-11-27 06:00 | 2012-11-29 06:00 | 200 | 21.3333 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-01-18 16:38 | 2013-01-18 20:36 | 200 | 1.7616 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-03-22 00:59 | 2013-03-22 05:07 | 200 | 1.8356 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-03-22 10:49 | 2013-03-22 15:35 | 200 | 2.1156 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-03-22 18:24 | 2013-03-22 19:13 | 200 | 0.36889 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-03-22 19:31 | 2013-03-22 21:10 | 200 | 0.73333 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-04-23 21:08 | 2013-04-24 00:09 | 250 | 1.8401 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-04-01 | 2013-04-30 23:59 | 160 | 280.9691 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-05-01 | 2013-08-31 23:59 | 160 | 1151.9935 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-08-12 08:00 | 2013-09-20 06:00 | 250 | 569.5122 | 2005-04-01 | PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-09-01 | 2013-11-01 06:00 | 160 | 573.6585 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2013-11-01 06:00 | 2014-03-31 06:00 | 200 | 1600 | 2005-04-01 | FO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
2014-03-31 06:00 | 2014-05-01 06:00 | 160 | 290.3415 | 2005-04-01 | FO | 283.3171 | 0 | 0 | 0 | 0 | 0 | 0 | 283.3171 |  |  | 283.3171
2014-05-01 06:00 | 2013-08-31 23:59 | 160 | -2268.8846 | 2005-04-01 | FO | -2268.8846 | 0 | 0 | -2268.8846 | 0 | 0 | 0 | 0 |  |  | -2268.8846
2014-05-12 22:00 | 2014-05-13 07:00 | 250 | 5.4878 | 2005-04-01 | FO | 5.4878 | 0 | 0 | 5.4878 | 0 | 0 | 0 | 0 |  |  | 5.4878
2014-05-14 05:53 | 2014-05-14 08:22 | 250 | 1.5142 | 2005-04-01 | FO | 1.5142 | 0 | 0 | 1.5142 | 0 | 0 | 0 | 0 |  |  | 1.5142
2014-05-18 06:00 | 2014-05-18 14:00 | 250 | 4.878 | 2005-04-01 | PO | 0 | 0 | 4.878 | 4.878 | 0 | 0 | 0 | 0 |  |  | 4.878
2014-03-31 07:30 | 2014-04-07 15:30 | 250 | 107.3171 | 2005-04-01 | PO | 0 | 0 | 97.2561 | 0 | 0 | 0 | 0 | 97.2561 |  |  | 97.2561
2014-06-29 05:24 | 2014-06-29 13:58 | 250 | 5.2236 | 2005-04-01 | FO | 5.2236 | 0 | 0 | 5.2236 | 0 | 0 | 0 | 0 |  |  | 5.2236
2014-07-05 08:30 | 2014-08-29 16:30 | 250 | 809.7561 | 2005-04-01 | PO | 0 | 0 | 809.7561 | 809.7561 | 0 | 0 | 0 | 0 |  |  | 809.7561
2014-11-03 08:30 | 2014-11-04 16:30 | 250 | 19.5122 | 2005-04-01 | PO | 0 | 0 | 19.5122 | 19.5122 | 0 | 0 | 0 | 0 |  |  | 19.5122
122.9993
2951.9833
1151.9935

## Sheet3 (hidden)
| 2004/5 | 2005/6 | 2006/7 | 2007/8 | 2008/9 | 2009/10
FO | 7 | 13 | 8 | 5 | 1 | 10
Hours | 4 | 24.82 | 9.38 | 15.95 | 0.92 | 22.36